## Table 1
Table 1: Customers Notified and De-energized1
Total Customers |  |  | MBL Program Customers | Counties | Tribes | Circuits |  |  | Damage/Hazard Count | CFI De-energized
Notified | De-energized | Canceled | De-energized | De-energized | De-energized | Transmission De-energized | Unique Distribution Circuits in Any Version of Scope | Distribution Circuits De-energized
35,072 2 | 17,367 3 | 17,850 4 | 1136 | 21 | 3 | 3 | 133 | 97 | 2 damages 1 hazard | 601
1 The information, times and figures referenced in this report are based on the best information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.
2 Of the 35,072 customers notified of planned PSPS impact, 77 customers received a notice that they may be de-energized, did not receive a cancellation notice and are not counted as a de-energized customer. This customer set is comprised of false positive notifications as reported in Section 5.5, customers mitigated from experiencing long-duration PSPS outages, and customers who stopped service or stopped having valid contact information by the time of cancellation notifications or de-energization.
3 Of the 17,367 customers de-energized, 222 customer did not receive any notifications before de-energization. This is comprised of 169 notification failures and 53 customers with no valid contact information at the time of these notifications. See Section 5.5 for more information.
4 This count includes customers canceled without being de-energized. This does not include the 15 customers who received cancellation notifications and were also de-energized, which includes 10 cases of false negative communications as reported in Section 5.7 and five customers who were properly notified that they were back in scope after the previous cancellation.

## Table 2
Table 2: 2024 PSPS Risk-Benefit Consequence Modelling Considerations
Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outage.1
Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
Table 3: Notification Descriptions
Type of Notification | Recipients | Description
PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs,1 transmission-level customers, and municipal utilities | On October 14, 2024, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E is monitoring an increased potential of PSPS outages. Following PG&E’s activation of its EOC, the following was completed:
•PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS.
•PG&E sent notifications to other Public Safety Partners2 via call, text, and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When weather is anticipated to pass.
o Estimated Time of Restoration (ETOR).
o Links to the PSPS Portal where PSPS-specific maps and information are available.
WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers) transmission-level customers, and municipal utilities | During this time, the following was completed:
• PG&E submitted a PSPS Notification Form to Cal OES.
•PG&E sent notifications to other Public Safety Partners, transmission-level customers, municipal utilities, and all customers via call, text message and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When the adverse weather is anticipated to pass.
o ETOR
o For Public Safety Partners only: Links to the PSPS Portal.
o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support and the Portable Battery Program.
o For Transmission Customers only: Transmission Substation Name and Line name serving substation.
• PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL Program customers, SIV Program customers) transmission-level customers, and municipal utilities | During this time, the following was completed:
• PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize.
• PG&E sent notifications to other Public Safety Partners, transmission-level customers, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.”
• PG&E sent notifications to MBL Program customers, including tenants of master metered accounts and SIV Program customers every hour until the customer confirmed receipt of the notification.
• PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would be shut off.
Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers3, and municipal utilities | When shut off was initiated, the following was completed:
•PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated.
• Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES representatives that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized.
• PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers.
• PG&E sent notifications to other Public Safety Partners, municipal utilities, transmission-level customers and customers via call, text messages, and e-mail, which included:
o Impacted addresses (for customers only).
o De-energization time.
o When the adverse weather is anticipated to pass.
o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the Portable Battery Program.
Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | After the weather had passed and areas were deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission-level customers26, municipal utilities and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include:
o New field or meteorology conditions.
o Damage was found during patrols and repair is needed.
Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | GCC conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including MBL Program customers and SIV Program customers, were restored, they received notifications via call, text and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages
23 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL Program and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
24 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.
25 Transmission-level customers receive a GCC live call before de-energization and prior to re-energization.
26 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 4
Table 4: Customer Notification Timeline Summary
Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Distributed by:
Pre-De-energization (Prior) | 72-48 hours | Tribal/Local Governments and CCAs* | 2024-10-15 07:21 | Priority |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-15 21:17 | Priority |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-16 09:53 | Priority |  | PG&E
|  | Public Safety Partners** | 2024-10-15 06:45 | Priority |  | PG&E
|  | Public Safety Partners** | 2024-10-15 11:45 | Priority | Only Shared Customers that are Public Safety Partners received this notification (SO. CAL EDISON NO. 3 1101). | SCE
|  | Public Safety Partners** | 2024-10-15 21:10 | Priority |  | PG&E
|  | Public Safety Partners** | 2024-10-16 09:45 | Priority |  | PG&E
| 48-24 hours | Tribal/Local Governments and CCAs* | 2024-10-15 19:56 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-15 19:33 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
|  | Public Safety Partners** | 2024-10-15 19:40 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-16 08:08 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-16 10:26 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
|  | All Customers*** | 2024-10-15 19:33 | Watch | Auberry 1101 | SCE
|  | All Customers*** | 2024-10-15 19:33 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
|  | All Customers*** | 2024-10-15 19:42 | Watch |  | PG&E
|  | All Customers*** | 2024-10-16 08:07 | Watch |  | PG&E
|  | All Customers*** | 2024-10-16 10:25 | Watch | Auberry 1101 | SCE
|  | All Customers*** | 2024-10-16 10:26 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
| 24-12 hours2 | Tribal/Local Governments and CCAs* | 2024-10-16 07:58 | Watch |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-16 17:09 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-16 18:03 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-16 18:27 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-10-17 10:26 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
|  | Public Safety Partners** | 2024-10-17 04:14 | Watch |  | PG&E
|  | All Customers*** | 2024-10-16 17:52 | Watch |  | PG&E
|  | All Customers*** | 2024-10-17 09:34 | Watch | Auberry 1101 | SCE
|  | All Customers*** | 2024-10-17 10:26 | Watch | SO. CAL EDISON NO. 3 1101 | SCE
|  | All Customers*** | 2024-10-17 04:09 | Watch |  | PG&E
| 4-1 hours | Tribal/Local Governments and CCAs* | 2024-10-17 07:49 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 09:49 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 12:50 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 14:10 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 16:37 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 18:12 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 21:05 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 22:06 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-18 01:42 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-18 13:36 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 07:58 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 10:01 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 13:05 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 14:18 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 17:15 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 18:15 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 20:38 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 22:12 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-17 23:03 | Warning | SO. CAL EDISON NO. 3 1101 | SCE
|  | Public Safety Partners** | 2024-10-18 01:50 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-10-18 13:34 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 07:54 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 09:59 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 13:04 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 14:17 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 17:15 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 18:15 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 20:38 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 22:09 | Warning |  | PG&E
|  | All Customers*** | 2024-10-17 22:56 | Warning | Auberry 1101 | SCE
|  | All Customers*** | 2024-10-17 23:03 | Warning | SO. CAL EDISON NO. 3 1101 | SCE
|  | All Customers*** | 2024-10-18 01:48 | Warning |  | PG&E
|  | All Customers*** | 2024-10-18 13:33 | Warning |  | PG&E
Initiation (During) | When De-energization is initiated | Public Safety Partners** | 2024-10-17 13:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 13:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 13:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 13:45 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 14:02 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 14:19 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 14:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 15:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 15:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 16:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 16:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 17:20 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 17:39 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 17:40 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 17:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 18:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 18:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 18:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 18:45 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 19:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 19:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 19:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 19:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 20:06 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 20:31 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 20:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 21:03 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 21:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 21:30 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-17 22:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 00:15 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 00:30 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 00:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 01:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 02:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 03:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 03:15 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 08:30 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 17:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 20:00 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 20:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-18 20:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 13:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 13:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 13:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 13:45 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 14:02 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 14:19 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 14:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 15:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 15:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 16:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 16:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 17:20 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 17:39 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 17:40 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 17:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 18:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 18:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 18:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 18:45 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 19:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 19:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 19:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 19:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 20:06 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 20:31 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 20:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 21:03 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 21:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 21:30 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-17 22:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 00:15 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 00:30 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 00:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 01:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 02:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 03:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 03:15 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 08:30 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 17:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 20:00 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 20:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-18 20:31 | Power Off |  | PG&E
Initiation (During) | Immediately before re-energization | Tribal/Local Governments and CCAs* | 2024-10-18 11:41 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-19 14:36 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-17 16:59 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-19 16:55 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | All Customers*** | 2024-10-17 16:59 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | All Customers*** | 2024-10-19 16:55 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-17 15:40 | ETOR Update | First ETOR Update Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-20 12:21 | ETOR Update | Last ETOR Update Notification sent. | PG&E
|  | All Customers*** | 2024-10-17 15:40 | ETOR Update | First ETOR Update Notification sent. | PG&E
|  | All Customers*** | 2024-10-20 12:21 | ETOR Update | Last ETOR Update Notification sent. | PG&E
Restoration (After) | After re-energization was completed | Public Safety Partners** | 2024-10-17 14:46 | Restore | First initial Restoration Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-20 17:03 | Restore | Last initial Restoration Notification sent. | PG&E
|  | All Customers*** | 2024-10-17 14:46 | Restore | First initial Restoration Notification sent. | PG&E
|  | All Customers*** | 2024-10-20 17:03 | Restore | Last initial Restoration Notification sent. | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-20 16:59 | Restore |  | PG&E
Cancelation | Within 2 hours of decision to cancel | Tribal/Local Governments and CCAs* | 2024-10-16 06:55 | Cancel | Only Tribal/Local Governments and CCAs removed from scope received cancel notification. The decision to descope these customers was made on 19/16/2024 at 05:41 AM. | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-17 02:38 | Cancel | Only Tribal/Local Governments and CCAs removed from scope received cancel notification. The decision to descope these customers was made on 19/17/2024 at 02:15 AM. | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-18 15:20 | Cancel | Only Tribal/Local Governments and CCAs removed from scope received cancel notification. The decision to descope these customers was made on 10/18/2024 at 03:06 PM. | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-10-19 09:50 | Cancel | Only Tribal/Local Governments and CCAs removed from scope received cancel notification. The decision to descope these customers was made on 10/19/2024 at 09:35 AM. | PG&E
|  | Public Safety Partners** | 2024-10-15 18:30 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 18:08. | PG&E
|  | Public Safety Partners** | 2024-10-16 07:00 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 05:41. | PG&E
|  | Public Safety Partners** | 2024-10-17 02:57 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 02:15. | PG&E
|  | Public Safety Partners** | 2024-10-18 05:34 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 5:20. | PG&E
|  | Public Safety Partners** | 2024-10-18 15:29 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 15:06. | PG&E
|  | Public Safety Partners** | 2024-10-19 10:40 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made on 10/18/2024 at 9:35. | PG&E
|  | Public Safety Partners** | 2024-10-19 11:43 | Cancel | Only Shared Customer Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers (SO. CAL EDISON NO. 3 1101). | SCE
|  | All Customers*** | 2024-10-15 18:30 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 18:08. | PG&E
|  | All Customers*** | 2024-10-16 07:00 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 5:41. | PG&E
|  | All Customers*** | 2024-10-17 02:57 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 2:15. | PG&E
|  | All Customers*** | 2024-10-18 05:34 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 5:20. | PG&E
|  | All Customers*** | 2024-10-18 15:29 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 15:06. | PG&E
|  | All Customers*** | 2024-10-19 10:09 | Cancel | Only Shared Customers removed from scope received the cancel notification. The decision to descope these customers (Auberry 1101). | SCE
|  | All Customers*** | 2024-10-19 10:40 | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 9:35. | PG&E
|  | All Customers*** | 2024-10-19 11:43 | Cancel | Only Shared Customers removed from scope received the cancel notification. The decision to descope these customers (SO. CAL EDISON NO. 3 1101). | SCE
Ad Hoc Notification | N/A | Customers incorrectly notified | 10/18/2024 6:54 | Ad Hoc | Only customers who received the incorrect restoration notification received this ad hoc notification. | PG&E
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators.
**A subset of Public Safety Partners, including water, wastewater, and communication service providers.
***All Customers, including MBL Program customers and SIV Program customers.
1 D.19-05-042, Appendix A, Timing of Notification.
2 While not a CPUC requirement, PG&E provides an additional 24-12-hour notification to Tribal/Local Governments, Public Safety Partners and Customers.

## Table 5
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted1
Designation | Total Number of customers2 | Notification Attempts Made3 | Timing of Attempts4 (PDT) | Who made the Notification Attempt | Successful Positive Notification5
MBL Program6 | 1948 | 1,927 Watch Notifications | 2024-10-15 19:43 | PG&E | 1,859 Watch Notifications
|  | 1,527 Warning Notifications | 2024-10-16 20:10 |  | 1,273 Warning Notifications
|  | 3,454 Overall Notifications | 2024-10-15 19:43 |  | 3,132 Overall Notifications
MBL behind a master meter7 | 18 | 18 Watch Notifications | 2024-10-15 19:43 | PG&E | 16 Watch Notifications
|  | 12 Warning Notifications | 2024-10-16 17:59 |  | 9 Warning Notifications
|  | 30 Overall Notifications | 2024-10-15 19:43 |  | 25 Overall Notifications
SIV Program | 928 | 928 Watch Notifications | 2024-10-15 19:43 | PG&E | 869 Watch Notifications
|  | 719 Warning Notifications | 2024-10-16 20:08 |  | 565 Warning Notifications
|  | 1,647 Overall Notifications | 2024-10-15 19:43 |  | 1,434 Overall Notifications
1 Counts of Notification Attempts Made will not reflect the actual total number of customers notified as both MBL Program and SIV Program customers can appear in both subset groups.
2 Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
3 Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
4 Initial start time notification was sent.
5 PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
6 Residential tenants of master-metered customers can also qualify for Medical Baseline quantities. The Medical Baseline category for the purposes of Table 5 does not include MBL Program customers who are master meter tenants.
7 PG&E has additional processes in place to ensure MBL Program customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 6
Table 6: Outcomes of Notifications to De-energized Medical Baseline Program Customers
Count | Type of Notifications to De-energized MBL Program Customers1 | Description
1116 | Total De-energized MBL Program Customers | The number of customers de-energized who participate in PG&E’s MBL Program.
1116 | Total Notifications Attempted / Sent | The total sum of automated notifications attempted via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls.
0 | Total Notifications Not Attempted / Sent | Total MBL Program customers de-energized that PG&E did not attempt to notify.
1114 | Total Notifications Delivered | The total sum of automated notifications sent via call, text, and e-mail.
2 | Total Notifications Not Delivered2 | Total MBL Program customers de-energized whose notification was not delivered.
762 | Total Notifications Initially Acknowledged | The total sum of automated notifications sent via call, text, and email where notification was acknowledged.
2146 | Total In-Person Visits/Doorbell Rings and Live Agent Phone Calls | Total attempted doorbell ring for impacted MBL Program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger3 This includes call attempts made by Live Agent representatives to MBL Program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit. Refer to Table 7 for the detailed breakdown of this category.
1103 | Total Notifications Received | Customers who acknowledged their notification by taking one of the following actions: answered an automated or Live Agent phone call, responded to a text message, opened an e-mail, or greeted an in-person doorbell ring (excludes voicemails left, text message delivered only and not confirmed, door hanger left).
13 | Total Notifications Not Received | Total MBL Program customers who did not confirm receipt/acknowledge their automated notifications, Live Agent phone calls or in-person doorbell ring. Customers who did not answer a doorbell ring were left a door hanger.
1 Based on SPID.
2 Customers received Doorbell Rings.
3 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 7
Table 7: Count and Type of Additional Notifications to De-energized Medical Baseline Program Customers
Count | Type of Additional Notifications to Impacted Medical Baseline Customers1 | Description
542 | Total In-Person Visits / Doorbell Rings | Doorbell ring attempts to impacted MBL Program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.2
1604 | Live Agent Phone Calls | Calls made by Live Agent representatives to MBL Program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit.
1 Based on SPID.
2 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 8
Table 8: Notification Failure Causes
Notifications Sent to: | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
Public Safety Partners excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 0 | No failures.
| Entities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Entities who did not receive any notifications before de-energization | 0 | No failures.
| Entities who were not notified immediately before re-energization | 0 | No failures.
| Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
CFI2 | Facilities who did not receive 48-to 72-hour priority notification | 14 | See Table 8A and 8B.
| Facilities who did not receive 1–4-hour imminent notification | 2 | See Table 8A.
| Facilities who did not receive any notifications before de-energization | 2 | See Table 8A.
| Facilities who were not notified at de-energization initiation | 29 | See Table 8D and 8E.
| Facilities who were not notified immediately before re-energization | 197 | See Table 8D and 8F.
| Facilities who were not notified when re-energization is complete | 10 | See Table 8D and 8G.
| Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
All other affected customers | Customers who did not receive 24–48-hour advance notifications | 167 | See Table 8A.
| Customers who did not receive 1–4-hour imminent notifications | 168 | See Table 8A and 8C.
| Customers who did not receive any notifications before de-energization | 167 | See Table 8A.
| Customers who were not notified at de-energization initiation | 324 | See Table 8D and 8E.
| Customers who were not notified immediately before re-energization | 4146 | See Table 8D and 8F.
| Customers who were not notified when re-energization is complete | 294 | See Table 8D and 8G.
| Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 PG&E Customers 2 SCE Customers | SCE’s notification vendor located a special character in the cancel message causing processing issues. Once the special character was removed, the notification re-launched and delivered the notification eight minutes after the 2-hour compliance window.
1 Only includes Tribes, cities, counties, and CCAs.
2 Includes Public Safety Partners who are critical facilities and infrastructure customers.

## Table 8A
Table 8A: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Any Notifications Before De-Energization
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
2 | 165 | These customers were not planned to be de-energized based on the normal circuit configuration. However, these customers were on an abnormal switching configuration that was not properly accounted for at the time of de-energization, and therefore, did not receive any notifications prior to de-energization. We will review our processes to properly account for abnormal switching with the responsible personnel and consider additional training.
0 | 2 | Our data system for pre-outage PSPS notifications had not yet registered that these customers were in service. Therefore, these customers were not identified as impacted by PSPS and did not receive any notifications prior to de-energization. However, these customers did receive notifications at the time of the outage and post-outage.
12 | The root cause of these failures has not been identified and is still under investigation with our notification vendor. We will report our findings in the 2024 PSPS Post-Season Report. | The root cause of these failures has not been identified and is still under investigation with our notification vendor. We will report our findings in the 2024 PSPS Post-Season Report.

## Table 8B
Table 8B: Explanation of Failures for CFI Who Did Not Receive 48-to 72-Hour Priority Notification
Count of Critical Facilities | Explanation
12 | The root cause of these failures has not been identified and is still under investigation with our notification vendor. We will report our findings in the 2024 PSPS Post-Season Report.

## Table 8C
Table 8C: Explanation of Failures for All Other Affected Customers Who Did Not Receive 1-4-Hour Imminent Notifications
Count of All Other Affected Customers | Explanation
1 | A custom notification file provided to our vendor (Message Broadcast) was not launched. We plan to coordinate with Message Broadcast to address this process error.

## Table 8D
Table 8D: Explanation of Failures for CFI and All Other Affected Customers Who Were Not Notified at De-energization Initiation, Immediately Before Re-energization, and When Re-energization was Complete
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
4 | 24 | For these customers, our internal outage management system used for in-outage and post-outage notifications was not aligned with actual field conditions. Therefore, these customers did not receive notifications after their outage began. We plan to correct our systems for these customers to ensure they align with actual field conditions.
2 | 2 | These customers were impacted by a non-PSPS outage shortly before the start of the planned PSPS outage. We are still investigating why this resulted in these notification failures for the PSPS outage. We will report our findings in the 2024 PSPS Post-Season Report.
0 | 5 | The root cause of these failures has not been identified and is still under investigation. We will report our findings in the 2024 PSPS Post-Season Report.

## Table 8E
Table 8E: Explanation of Failures for CFI and All Other Affected Customers Who Were Not Notified at De-energization Initiation
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
23 | 292 | These customers were not notified at de-energization initiation. The root cause of these failures has not been identified and is still under investigation. We will report our findings in the 2024 PSPS Post-Season Report.
0 | 1 | These customers were not notified at de-energization initiation. The root cause of these failures has not been identified and is still under investigation. We will report our findings in the 2024 PSPS Post-Season Report.

## Table 8F
Table 8F: Explanation of Failures for CFI and All Other Affected Customers Who Were Not Notified Immediately Before Re-energization
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
11 | 80 | These customers were not notified immediately before re-energization due to a categorization error in our internal outage platform.
160 | 3128 | The root cause of these failures has not been identified and is still under investigation with our notifications vendor. We will report our findings in the 2024 PSPS Post-Season Report.
19 | 837 | The root cause of these failures has not been identified and is still under investigation. We will report our findings in the 2024 PSPS Post-Season Report.
1 | 70 | These customers did not receive this notification until after restoration. This was because the categorization change in our internal outage platform was performed shortly prior to re-energization, and did not leave enough time for this notification to be sent prior to re-energization. This categorization change can only be performed after All Clear has been declared and patrolling has begun. For 58 “Other Affected Customers” in this group, this was because these customers were restored less than one hour after All Clear was declared.

## Table 8G
Table 8G: Explanation of Failures for CFI and All Other Affected Customers Who Were Not Notified When Re-energization was Complete
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
4 | 257 | The root cause of these failures has not been identified and is still under investigation with our notifications vendor. We will report our findings in the 2024 PSPS Post-Season Report.
0 | 6 | The root cause of these failures has not been identified and is still under investigation. We will report our findings in the 2024 PSPS Post-Season Report.

## Table 9
Table 9: PSPS Portal Time & Date for Map Sharing
Date | Time PDF and GIS Maps Shared (PDT)
2024-10-15 | 5:53
2024-10-15 | 18:00
2024-10-16 | 6:47
2024-10-17 | 09:45*
2024-10-18 | 15:22
2024-10-19 | 9:51
*PG&E’s ability to share GIS and PDF Maps on the PSPS Portal was delayed by a systemwide outage by our vendor, Environmental Systems Research Institute, Inc. (ESRI). This outage was reported on October 16, 2024, at 17:37 and resolved on October 17, 2024, at 09:30. During this period, PG&E’s Public Safety Specialists had appropriate maps and information available to share with agency partners impacted by this PSPS.

## Table 10
Table 10: PSPS Notifications Submitted to Cal OES
Date | Time PDF and GIS Maps Shared (PDT)
2024-10-15 | 5:49
2024-10-15 | 6:40
2024-10-15 | 14:42
2024-10-16 | 6:25
2024-10-16 | 15:01
2024-10-17 | 2:26
2024-10-17 | 6:41
2024-10-17 | 11:13
2024-10-17 | 14:23
2024-10-17 | 17:08
2024-10-17 | 19:04
2024-10-17 | 20:44
2024-10-17 | 22:03
2024-10-18 | 1:19
2024-10-18 | 3:22
2024-10-18 | 7:01
2024-10-18 | 9:09
2024-10-18 | 11:07
2024-10-18 | 15:09
2024-10-18 | 15:24
2024-10-18 | 23:30
2024-10-19 | 7:06
2024-10-19 | 9:59
2024-10-19 | 11:21
2024-10-19 | 14:27
2024-10-20 | 8:41
2024-10-20 | 13:33

## Table 11
Table 11: PSPS Notifications Submitted to CPUC
Date | Time PDF and GIS Maps Shared (PDT)
2024-10-15 | 5:37
2024-10-16 | 5:57
2024-10-17 | 2:33
2024-10-17 | 8:34
2024-10-17 | 13:33
2024-10-17 | 16:39
2024-10-17 | 17:33
2024-10-17 | 18:43
2024-10-17 | 19:35
2024-10-17 | 20:13
2024-10-17 | 21:11
2024-10-17 | 23:53
2024-10-18 | 2:15
2024-10-18 | 7:42
2024-10-18 | 8:49
2024-10-18 | 15:15
2024-10-18 | 19:54
2024-10-19 | 9:45
2024-10-19 | 15:27
2024-10-20 | 16:55

## Table 12
Table 12: Customer Notifications Based on Language Preference
Language | Total Notifications1 | Percent
English | 1880483 | 99.5%
Spanish | 8152 | 0.4%
Chinese (Mandarin & Cantonese) | 259 | 0.014%
Vietnamese | 36 | 0.002%
Korean | 28 | 0.001%
Portuguese | 28 | 0.001%
Arabic | 19 | 0.001%
Total | 1889005 | 100%
1 Total notifications do not include doorbell rings and Live Agent phone calls.

## Table 13
Table 13: Call Center Support Services1
Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls (seconds) | Number of Calls Handled by Call Center Translation Services | Number of Languages Supported by Call Center Translation Services
94319 | 1133 | 6 | 1276 | 240+
1 Metrics are provided from October 15, 2024, through October 20, 2024.

## Table 14
Table 14: Generators Available for Critical Facilities and Infrastructure Customers
Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
Diesel Generator | 2 | 0.065 | 31 | 2 units on reserve in San Leandro.
Diesel Generator | 1 | 0.125 | 25 | 1 unit on reserve in San Leandro.
Diesel Generator | 4 | 0.2 | 22.9 | 4 units on reserve in San Leandro.
Diesel Generator | 1 | 0.275 | 26 | 1 unit on reserve in Sacramento.
Diesel Generator | 2 | 0.57 | 24.1 | 2 units on reserve in San Leandro.
Diesel Generator | 1 | 1.5 | 10 | 1 unit on reserve in Martinez.
Diesel Generator | 7 | 1 | 35 | 3 units pre-staged at an ICU Hospital, 4 units on reserve in Sacramento.
Diesel Generator | 8 | 1.14 | 24 | 8 units on reserve in San Leandro.
Diesel Generator | 13 | 2 | 27.7 | 13 units on reserve, 5 at San Leandro and 8 at Sacramento.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 15
Table 15: Critical Facility and Infrastructure Customers Energized with Backup Generation
County | Site Type | Generation Deployed | Duration of Operation (Hrs.) | Reason Deployed
Shasta | Cal Fire Happy Valley Fire Center | 0.125 | 0:00 | High risk to Essential Emergency Response and Support Facilities.
Tehama | Cal Fire Red Bank Station | 0.056 | 38:45 | High risk to Essential Emergency Response and Support Facilities.
Monterey | San Antonio Public School | 0.2 | 44:03 | High risk to public safety.
Williams | Cortina Rancheria Indian Reservation | 0.056 | 72:45 | High risk to public safety.
Colusa | Cortina Rancheria Indian Reservation | 0.056 | 73:45 | High risk to public safety.
Colusa | Cortina Rancheria Indian Reservation | 0.056 | 74:30 | High risk to public safety.
Solano | Residence Vacaville | 0.1 | 62:05 | High risk to public safety.
Sonoma | City of Cloverdale Wastewater Treatment Plant | 0.57 | 0:00 | High risk of environmental hazard.
Butte | Residence Yankee Hill | 0.056 | 45:17 | High risk to public safety.
Colusa | Elk Creek Elementary School | 0.2 | 75:15 | High risk to public safety.
Colusa | Elk Creek Junior High School | 0.35 | 77:05 | High risk to public safety.
Tehama | Flournoy Elementary School | 0.2 | 68:30 | High risk to public safety.
Napa | Angwin Distribution Microgrid | 0.5 | 63:35 | High risk to public safety.
Glenn | Residence Orland | 0.065 | 67:05 | High risk to public safety.
Colusa | Stonyford Community Hall | 0.032 | Intermittent 10/17/24 - 10/19/24 | High risk to public safety.

## Table 16
Table 16: Number and Nature of Complaints due to the October 17 – 20, 2024 PSPS
Nature of Complaints | Number of Complaints
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 78
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamics of weather conditions | 109
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL Program populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 42
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 287
Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers and other assistance provided by utility to mitigate impact of PSPS. | 17

## Table 17
Table 17: Count and Type of Claim(s) Received
Description of Claims | Number of Claims
Business Interruption / Economic Loss | 4
Food Loss Only | 22
Property Damage | 2

## Table 18
Table 18: Weather All-Clear Times
All-Clear Zones | Weather All-Clear Date and Time (PDT)
241B, 245C, 180C | 2024-10-18 07:26
246D, 246B | 2024-10-18 14:55
170B, 177D, 180D, 180H, 180J, 241A, 245A, 246C, 247C, 248B, 295A, 525, 530F, 530F, 530J, 565, 570B | 2024-10-19 05:28
180I, 180J, 241C, 247A, 247C, 280A, 280B, 518B, 520C, 530E, 553, 585 | 2024-10-19 08:53
175C, 175E, 177B, 177E, 177F, 177G, 246A, 246G, 280C, 280G, 540A | 2024-10-19 10:09
154D, 175D, 245B, 246I, 248A, 285A, 520B, 530A, 530D | 2024-10-19 12:00
175B, 177C, 530C, 530B | 2024-10-19 13:07
175F, 175G, 177A, 246H, 280H | 2024-10-19 14:23
175H | 2024-10-19 15:20

## Table 19
Table 19: Circuits PG&E was Unable to Restore within 24 Hours of the Weather All-Clear
Circuit Name | Reason the Utility was Unable to Restore the Circuit Within 24 Hours
SILVERADO 2104 | A portion of Silverado 2104 was not restored within 24 hours due to rugged mountainous terrain in portions of the circuit. Additionally, per our procedures,1 we are not able to perform helicopter patrols past sunset due to safety concerns. Therefore we reconvened patrols during sunrise on October 20, 2024. Restoration of the entire circuit was completed around 13:18 PDT.
1 Helicopter Operations Field Manual AVI-3001M Rev 2, Section 1.14.2, dated 10-21-24.

## Table 20
Table 20: Temporary Microgrids
Temporary Microgrid | Generation Deployed | Customers Energized
Angwin (Napa County) | 0.5 MW | 48

## Table 21
Table 21: Lessons Learned from the PSPS
Issue | Discussion | Resolution
Customer Notifications | Due to an oversight during a manual review of abnormal circuit conditions, 167 customers were not notified of de-energization (as reported in Table 8A). | We plan to review processes with responsible personnel and consider additional training.
Technology | ESRI experienced an enterprise-wide technology disruption that impacted a Python script PG&E utilizes to share customer maps on the PSPS Portal. | PG&E detected the issue on October 16 at 17:37 PDT and resolved it on October 17 at 09:30 PDT. PG&E has implemented a new process for sharing PDF Maps and limited GIS layers on the PSPS Portal in the event technology is down during a future PSPS.

## Table 22
Table 22: Maximum Wind Gusts Recorded October 17 – 20, 2024 in Impacted Counties
County | Maximum Wind Gust (mph) | Station ID | Station Name
Alameda | 53 | PG674 | Mt. Alison
Alpine | 52 | 011PG | Bloods Ridge
Amadore | 31 | PG404 | China Gulch Road
Butte | 47 | JBGC1 | Jarbo Gap
Calaveras | 52 | STUC1 | Cottage
Colusa | 77 | 595PG | Goat Mountain
Contra Costa | 56 | PG696 | Diablo-Blackhawk
El Dorado | 75 | 287PG | Leek Spring Hill
Fresno | 88 | QUPC1 | Upper Providence
Glenn | 40 | PG845 | Road 65
Lake | 72 | PG652 | Santa Fe Geothermal
Madera | 35 | MTTC1 | Minarets
Mariposa | 38 | PG184 | Jordan Creek Road
Mendocino | 54 | PG990 | Cahto Peak
Merced | 35 | KMER | Castle Air Force Base
Monterey | 41 | PG360 | Williams Hill
Napa | 49 | PG358 | Knoxville
Nevada | 61 | 472PG | Grouse Ridge Lookout
Placer | 57 | PG698 | Cisco Buttes
Plumas | 45 | 498PG | Mount Hough
Sacramento | 36 | KSAC | Sacramento Executive Airport
San Benito | 41 | SRTC1 | Santa Rita
San Joaquin | 37 | KSCK | Stockton Metropolitan Airport
San Luis Obispo | 52 | PG633 | Old Creek Road
Santa Barbara | 61 | MTIC1 | Montecito
Santa Clara | 60 | PG608 | Mt. Umunhum
Santa Cruz | 52 | PG370 | Ormsey Cutoff Trail
Shasta | 41 | PG070 | Roud Mountain – Shasta
Sierra | 61 | SLEC1 | Saddleback
Solano | 57 | PG880 | Blue Ridge Road South
Sonoma | 79 | PG132 | Mt. St. Helena West
Stanislaus | 49 | 045PG | Mt. Oso
Tehama | 55 | CBXC1 | Colby Mountain
Tuolumne | 42 | MOUC1 | Mount Elizabeth
Yolo | 54 | PG490 | Bald Mountain Tower
Yuba | 39 | KMYV | Yuba County Airport

## Table A-1.1
Table A-1.1: Factors Considered in the Decision to Shut off Power for Each Distribution Circuit De-energized During the October 17 – 20, 2024 PSPS Event
Circuit Name | Time Place | Forecast | [9 empty] | Agency |  |  | Observed
|  | ws_ mph | temp_2m_f | flame_ length_ ft_8hr | rate_ of_ spread_chhr_8hr | rh_ 2m | prob_cat | dfm_ 10hr | dfm_ 100 hr | lfm_ chamise_new | cfpd | NOAA | RFW | GACC_High Risk | ws_ mph | wg_ mph | temp_f | RH_% | ws_ mph_ AC | wg_ mph_ AC | temp_f_AC | RH_%_AC | open_ psps_ tags | Tx impacts_yes_no | PSPS Potential Risk Consequence | PSPS Potential Benefit
ARBUCKLE 1101 | TP4 | 20 | 83 | 9.2 | 55.1 | 8.7 | 0.409 | 0.05 | 0.093 | 52 | 1.8 | 707 | 707 | 707 | 25 | 34 | 77 | 13 | 14 | 20 | 78 | 20 | Yes | No | 0.1 | 249.5
BIG BEND 1101 | TP14 | 18 | 81 | 9.2 | 42.8 | 10.1 | 0.663 | 0.051 | 0.102 | 60 | 4.2 | 2 | 328 | 122 | 30 | 47 | 80 | 11 | 26 | 42 | 82 | 13 | Yes | No | 0.9 | 198.6
BRENTWOOD 2105 | TP8 | 22 | 79 | 11.4 | 148.7 | 12.6 | 0.254 | 0.052 | 0.106 | 59 | 2 | 2845 | 2842 | 2845 | 39 | 53 | 77 | 9 | 17 | 22 | 68 | 20 | Yes | No | 0.5 | 2557.4
BUCKS CREEK 1103 | TP14 | 28 | 71 | 8.4 | 31.9 | 13.2 | 0.376 | 0.061 | 0.128 | 66 | 11.8 | No | 352 | No | 22 | 41 | 71 | 13 | 16 | 29 | 71 | 15 | Yes | No | 8 | 7.5
CALISTOGA 1101 | TP7 | 32 | 85 | 40.7 | 67.6 | 7.9 | 0.631 | 0.048 | 0.104 | 63 | 25 | No | 1697 | 1697 | 61 | 79 | 90 | 6 | 23 | 32 | 90 | 14 | Yes | No | 0.6 | 225.4
CALISTOGA 1102 | TP7 | 17 | 83 | 5.6 | 25.6 | 8.6 | 0.473 | 0.049 | 0.113 | 64 | 3.7 | No | 2235 | 2235 | 30 | 43 | 87 | 6 | 10 | 20 | 87 | 13 | Yes | No | 0.1 | 604.6
CALPINE 1144 | TP7 | 23 | 78 | 11.4 | 56.4 | 9.2 | 0.643 | 0.053 | 0.101 | 63 | 7.3 | No | 22 | 22 | 60 | 72 | 85 | 5 | 22 | 32 | 85 | 13 | Yes | No | 0.1 | 253.1
CALPINE 1146 | TP7 | 20 | 76 | 10.7 | 36.3 | 9.8 | 0.634 | 0.056 | 0.11 | 64 | 7.8 | No | 1 | 1 | 60 | 72 | 82 | 8 | 22 | 32 | 82 | 19 | Yes | No | 0 | 1248.6
CANTUA 1103 | TP12 | 20 | 78 | 10.1 | 121.6 | 13.6 | 0.203 | 0.048 | 0.091 | 56 | 0.8 | 201 | 8 | 16 | 28 | 45 | 81 | 9 | 18 | 30 | 81 | 11 | Yes | No | 0 | 245.9
CASTRO VALLEY 1108 | TP17 | 21 | 79 | 14.1 | 50.2 | 10.7 | 0.437 | 0.054 | 0.124 | 68 | 8.1 | 5300 | 5300 | 5300 | 39 | 53 | 77 | 8 | 17 | 22 | 77 | 13 | Yes | No | 0.3 | 188.2
CAYETANO 2109 | TP8 | 30 | 77 | 11.3 | 145.8 | 12.8 | 0.451 | 0.05 | 0.105 | 58 | 5.4 | 3150 | 3150 | 3150 | 39 | 56 | 76 | 10 | 26 | 35 | 74 | 13 | Yes | No | 0.7 | 3049.3
CLAYTON 2212 | TP8 | 24 | 78 | 14.7 | 150.1 | 12.3 | 0.52 | 0.052 | 0.102 | 57 | 5.5 | 3446 | 3446 | 3446 | 31 | 48 | 76 | 10 | 26 | 31 | 72 | 15 | Yes | No | 3.4 | 271.8
CLAYTON 2213 | TP8 | 21 | 78 | 8.9 | 64.1 | 12 | 0.377 | 0.053 | 0.113 | 61 | 3.5 | 3232 | 3232 | 3232 | 34 | 46 | 91 | 5 | 13 | 23 | 92 | 11 | Yes | No | 0 | 11416.1
CLOVERDALE 1102 | TP7 | 20 | 86 | 12.6 | 54.6 | 7.6 | 0.676 | 0.049 | 0.104 | 62 | 5.7 | No | 2470 | 2538 | 26 | 46 | 68 | 12 | 11 | 19 | 53 | 16 | Yes | No | 0.3 | 1067.6
COALINGA NO 2 1105 | TP12 | 30 | 79 | 14.3 | 127.6 | 13 | 0.245 | 0.048 | 0.091 | 55 | 2.4 | 196 | 193 | 129 | 26 | 39 | 80 | 8 | 18 | 25 | 82 | 19 | Yes | No | 0.3 | 93.6
CORNING 1101 | TP2 | 21 | 83 | 9.6 | 110.4 | 9.8 | 0.575 | 0.05 | 0.093 | 52 | 4.6 | 2226 | 2226 | 2226 | 31 | 47 | 82 | 3 | 17 | 25 | 83 | 20 | Yes | No | 4.4 | 119.9
CORNING 1102 | TP2 | 23 | 83 | 12.6 | 148.5 | 9.7 | 0.616 | 0.049 | 0.085 | 52 | 3.5 | 1693 | 1646 | 1693 | 23 | 36 | 80 | 8 | 18 | 28 | 81 | 17 | Yes | No | 1.4 | 152.4
CORTINA 1101 | TP4 | 20 | 84 | 10.8 | 76.6 | 8.3 | 0.466 | 0.048 | 0.089 | 51 | 1.5 | 259 | 259 | 259 | 30 | 47 | 73 | 11 | 26 | 42 | 74 | 14 | Yes | No | 0.1 | 258.4
CRESTA 1101 | TP14 | 19 | 73 | 6.9 | 29.6 | 12.1 | 0.48 | 0.058 | 0.117 | 64 | 10.6 | No | 8 | No | 24 | 38 | 83 | 7 | 14 | 25 | 83 | 14 | Yes | No | 0 | 108.5
DUNBAR 1101 | TP19 | 25 | 84 | 13 | 50.6 | 8.8 | 0.634 | 0.047 | 0.108 | 61 | 9.1 | No | 2420 | 2420 | 34 | 46 | 83 | 3 | 27 | 38 | 85 | 11 | Yes | No | 0.8 | 429.6
DUNBAR 1103 | TP19 | 24 | 84 | 13.4 | 54.5 | 8.6 | 0.588 | 0.049 | 0.118 | 63 | 12.9 | No | 2464 | 3297 | 25 | 34 | 77 | 13 | 14 | 20 | 78 | 20 | Yes | No | 0.4 | 1441.5
DUNNIGAN 1103 | TP4 | 19 | 82 | 8.9 | 43.3 | 8.8 | 0.557 | 0.05 | 0.093 | 52 | 2.1 | 306 | 306 | 899 | 32 | 46 | 83 | 5 | 22 | 34 | 83 | 17 | Yes | No | 0.1 | 250.2
ELK CREEK 1101 | TP3 | 23 | 82 | 16.7 | 112.1 | 9.3 | 0.525 | 0.048 | 0.088 | 50 | 2.9 | 896 | 858 | No | 9 | 26 | 73 | 10 | 4 | 7 | 73 | 11 | Yes | Yes | 4.6 | 71.4
FRENCH GULCH 1101 | TP1 | 15 | 77 | 9.9 | 52.9 | 13.5 | 0.593 | 0.058 | 0.102 | 66 | 4.2 | 253 | No | No | 16 | 30 | 77 | 8 | 10 | 16 | 77 | 9 | Yes | No | 0.9 | 46.1
FRENCH GULCH 1102 | TP1 | 19 | 79 | 9.1 | 39.5 | 12.4 | 0.463 | 0.055 | 0.098 | 63 | 1.9 | 38 | No | 1233 | 60 | 72 | 90 | 5 | 22 | 32 | 90 | 13 | Yes | No | 0.3 | 40.9
GEYSERVILLE 1102 | TP7 | 22 | 87 | 13.5 | 83.8 | 7.3 | 0.619 | 0.049 | 0.102 | 63 | 7.3 | No | 1233 | 1163 | 20 | 35 | 78 | 6 | 14 | 22 | 78 | 8 | Yes | No | 0.5 | 439.7
GIRVAN 1101 | TP1 | 19 | 82 | 9.6 | 94.5 | 10.8 | 0.604 | 0.049 | 0.084 | 55 | 1.8 | 1280 | 991 | 1965 | 25 | 37 | 82 | 3 | 18 | 26 | 83 | 14 | Yes | No | 1.6 | 575.6
GLENN 1101 | TP3 | 23 | 83 | 11.3 | 138.7 | 9.3 | 0.49 | 0.049 | 0.089 | 51 | 4.2 | 1965 | 4476 | 4476 | 40 | 60 | 75 | 10 | 30 | 40 | 65 | 14 | Yes | No | 2 | 47.2
HICKS 2101 | TP18 | 16 | 76 | 17.6 | 57.2 | 12.1 | 0.47 | 0.054 | 0.123 | 65 | 3.3 | 4476 | 3652 | 3652 | 32 | 46 | 85 | 6 | 15 | 24 | 85 | 16 | Yes | No | 0.4 | 2712.3
HIGHLANDS 1102 | TP7 | 16 | 80 | 14 | 67 | 9 | 0.593 | 0.053 | 0.108 | 57 | 1.9 | 16 | 2424 | 2424 | 33 | 49 | 80 | 6 | 24 | 45 | 80 | 15 | Yes | No | 0.1 | 4127.8
HIGHLANDS 1103 | TP20 | 24 | 79 | 11.1 | 54.2 | 9.3 | 0.643 | 0.054 | 0.102 | 57 | 5.4 | 35 | 2290 | 2290 | 21 | 35 | 81 | 8 | 12 | 26 | 82 | 14 | Yes | No | 0.2 | 3446.5
JAMESON 1102 | TP6 | 23 | 81 | 19.8 | 47.9 | 10.1 | 0.519 | 0.049 | 0.106 | 61 | 6.9 | 2290 | 2646 | 2650 | 21 | 33 | 81 | 8 | 12 | 26 | 82 | 14 | Yes | No | 0.1 | 3432.3
JAMESON 1105 | TP6 | 24 | 77 | 8.8 | 56.5 | 11.1 | 0.515 | 0.055 | 0.112 | 61 | 7.7 | 2650 | 604 | 604 | 29 | 39 | 76 | 10 | 6 | 9 | 58 | 23 | Yes | No | 0 | 15184.9
JOLON 1102 | TP12 | 20 | 79 | 12.4 | 80.3 | 11.8 | 0.451 | 0.055 | 0.102 | 59 | 1.6 | No | 16 | 16 | 23 | 31 | 76 | 10 | 6 | 7 | 58 | 23 | Yes | Yes | 3.6 | 18.6
JOLON 1103 | TP12 | 16 | 75 | 10.2 | 62.3 | 12.4 | 0.394 | 0.054 | 0.1 | 60 | 1.1 | No | 441 | 532 | 18 | 35 | 83 | 8 | 10 | 18 | 83 | 9 | Yes | Yes | 2.4 | 10.4
KESWICK 1101 | TP1 | 20 | 80 | 10.8 | 50.6 | 11.3 | 0.667 | 0.052 | 0.088 | 62 | 1.6 | 548 | 1368 | 1368 | 21 | 32 | 83 | 4 | 13 | 21 | 83 | 16 | Yes | No | 1.2 | 420.7
LAKEVILLE 1102 | TP19 | 24 | 83 | 9.6 | 92.9 | 8.8 | 0.534 | 0.05 | 0.116 | 64 | 5 | No | 1493 | 1493 | 30 | 40 | 82 | 7 | 25 | 32 | 83 | 17 | Yes | No | 0.4 | 4578.9
LOGAN CREEK 2102 | TP3 | 24 | 85 | 11.6 | 155.1 | 8.4 | 0.335 | 0.048 | 0.092 | 52 | 3.1 | 1493 | 2637 | 2637 | 28 | 41 | 76 | 10 | 6 | 12 | 72 | 15 | Yes | No | 0.2 | 212.6
LONE TREE 2105 | TP8 | 25 | 79 | 11.2 | 145.8 | 12.3 | 0.321 | 0.053 | 0.101 | 59 | 3 | 2637 | 2307 | 2307 | 40 | 60 | 72 | 14 | 30 | 40 | 65 | 14 | Yes | No | 0.2 | 3259.2
LOS GATOS 1107 | TP18 | 20 | 72 | 20 | 58.3 | 13.5 | 0.391 | 0.056 | 0.118 | 64 | 12.1 | 2303 | 586 | 586 | 25 | 38 | 78 | 9 | 17 | 23 | 78 | 17 | Yes | No | 0.7 | 74.1
MADISON 1105 | TP5 | 23 | 83 | 7.1 | 71.4 | 9 | 0.532 | 0.049 | 0.104 | 51 | 5.5 | 586 | 2188 | 2188 | 35 | 54 | 81 | 8 | 18 | 27 | 81 | 12 | Yes | No | 0 | 620.2
MADISON 2101 | TP5 | 24 | 83 | 8.7 | 88.8 | 8.8 | 0.533 | 0.049 | 0.089 | 53 | 3.4 | 2188 | 228 | 228 | 20 | 32 | 80 | 8 | 18 | 29 | 82 | 18 | Yes | No | 0.1 | 7402.1
MAXWELL 1102 | TP4 | 20 | 84 | 10.2 | 123.6 | 8.3 | 0.264 | 0.047 | 0.092 | 56 | 1.4 | 228 | 843 | 843 | 30 | 40 | 80 | 8 | 25 | 32 | 82 | 17 | Yes | No | 0.2 | 119.4
MAXWELL 1105 | TP4 | 21 | 84 | 11.4 | 145.5 | 8.4 | 0.382 | 0.047 | 0.091 | 53 | 2.4 | 843 | 2105 | 2105 | 61 | 79 | 90 | 6 | 23 | 32 | 90 | 14 | Yes | No | 0.1 | 185.1
MIDDLETOWN 1101 | TP7 | 26 | 81 | 20.4 | 65.2 | 8.8 | 0.643 | 0.052 | 0.097 | 62 | 13.7 | No | 4351 | 4351 | 43 | 53 | 80 | 9 | 14 | 20 | 81 | 12 | Yes | No | 1.4 | 518.8
MILPITAS 1109 | TP17 | 25 | 76 | 9.1 | 90.7 | 12.4 | 0.44 | 0.052 | 0.123 | 64 | 2.8 | 4351 | 1404 | 1409 | 41 | 57 | 86 | 7 | 19 | 28 | 86 | 14 | Yes | No | 0.9 | 937.8
MONTICELLO 1101 | TP5 | 25 | 83 | 29.2 | 65.3 | 9.1 | 0.643 | 0.048 | 0.102 | 58 | 5.6 | 1409 | 2911 | 2692 | 33 | 52 | 75 | 10 | 24 | 36 | 63 | 14 | Yes | No | 1.9 | 98.3
MORGAN HILL 2111 | TP18 | 18 | 76 | 17.7 | 47.7 | 12 | 0.511 | 0.055 | 0.12 | 64 | 7.6 | 2692 | 4936 | 2912 | 21 | 33 | 81 | 8 | 12 | 26 | 82 | 14 | Yes | No | 0.4 | 4072.6
NAPA 1112 | TP6 | 21 | 77 | 12.9 | 57.2 | 11.1 | 0.474 | 0.055 | 0.109 | 60 | 2.5 | 2673 | 2037 | 4936 | 39 | 56 | 75 | 10 | 26 | 35 | 76 | 14 | Yes | No | 0.1 | 20923.2
NORTH DUBLIN 2103 | TP8 | 25 | 77 | 10.8 | 137.8 | 12.4 | 0.342 | 0.052 | 0.122 | 64 | 3.6 | 4936 | 229 | 1383 | 31 | 53 | 78 | 12 | 22 | 40 | 80 | 14 | Yes | No | 0.2 | 12926.2
ORO FINO 1102 | TP14 | 26 | 75 | 13.8 | 21.6 | 11.6 | 0.269 | 0.057 | 0.128 | 64 | 5.8 | 1387 | 2524 | 256 | 11 | 26 | 65 | 19 | 5 | 9 | 49 | 29 | Yes | No | 2.1 | 9
PANOCHE 1103 | TP12 | 20 | 76 | 12.6 | 86.9 | 14.2 | 0.218 | 0.05 | 0.097 | 56 | 0.6 | 338 | 2071 | 2493 | 17 | 32 | 78 | 12 | 12 | 25 | 80 | 14 | Yes | No | 0.1 | 636
PARADISE 1105 | TP14 | 12 | 74 | 5.9 | 14 | 11.7 | 0.388 | 0.057 | 0.12 | 65 | 1.3 | 2507 | 2143 | 2071 | 25 | 39 | 86 | 7 | 10 | 17 | 86 | 12 | Yes | No | 0.2 | 92.9
PUEBLO 1104 | TP7 | 25 | 76 | 9.1 | 52.9 | 10.8 | 0.512 | 0.055 | 0.114 | 60 | 5.3 | 2068 | 2295 | 2143 | 25 | 39 | 88 | 7 | 10 | 17 | 88 | 12 | Yes | No | 0.2 | 4753.4
PUEBLO 1105 | TP7 | 24 | 79 | 9.8 | 52.8 | 10.1 | 0.606 | 0.054 | 0.116 | 62 | 7.7 | 1336 | 4710 | 2295 | 34 | 46 | 84 | 6 | 27 | 38 | 85 | 14 | Yes | No | 0.3 | 2453.9
PUEBLO 2102 | TP19 | 20 | 80 | 14.9 | 43.6 | 9.6 | 0.588 | 0.051 | 0.113 | 63 | 6.1 | 2 | 917 | 4710 | 24 | 38 | 83 | 7 | 14 | 25 | 83 | 12 | Yes | No | 0.3 | 245.4
PUEBLO 2103 | TP19 | 23 | 83 | 26.2 | 81 | 9.2 | 0.648 | 0.049 | 0.107 | 63 | 11.9 | No | 2206 | 917 | 41 | 57 | 76 | 7 | 24 | 33 | 77 | 18 | Yes | No | 1 | 317.5
PUTAH CREEK 1102 | TP5 | 22 | 83 | 7.8 | 76.3 | 9.1 | 0.523 | 0.048 | 0.092 | 51 | 14.1 | 917 | 1317 | 2206 | 23 | 40 | 76 | 9 | 13 | 26 | 77 | 18 | Yes | No | 0.7 | 5048.5
PUTAH CREEK 1103 | TP5 | 21 | 83 | 6.8 | 56.6 | 9.2 | 0.507 | 0.048 | 0.094 | 55 | 9.6 | 2206 | 2532 | 1317 | 25 | 38 | 76 | 9 | 17 | 26 | 77 | 18 | Yes | No | 0.2 | 45784.7
PUTAH CREEK 1105 | TP5 | 24 | 83 | 8.1 | 89.3 | 9 | 0.452 | 0.048 | 0.099 | 51 | 11.2 | 1317 | 1632 | 2532 | 28 | 41 | 77 | 12 | 17 | 26 | 77 | 11 | Yes | No | 0.1 | 2214.1
RAWSON 1103 | TP1 | 21 | 84 | 6.6 | 61.2 | 9.7 | 0.409 | 0.053 | 0.099 | 52 | 3.4 | 2532 | 2722 | 1632 | 29 | 43 | 82 | 7 | 16 | 22 | 84 | 14 | Yes | No | 0 | 4971.3
RED BLUFF 1101 | TP2 | 20 | 84 | 8.2 | 79.4 | 9.8 | 0.448 | 0.052 | 0.094 | 52 | 1.6 | 1632 | 1939 | 2722 | 29 | 43 | 82 | 7 | 16 | 22 | 84 | 14 | Yes | No | 0.3 | 7670.2
RED BLUFF 1103 | TP2 | 20 | 83 | 7.6 | 75 | 9.8 | 0.537 | 0.052 | 0.092 | 52 | 3 | 2722 | 2099 | 1939 | 29 | 43 | 79 | 9 | 16 | 20 | 79 | 7 | Yes | No | 0.7 | 1856.7
RED BLUFF 1105 | TP1 | 21 | 84 | 13.5 | 64.4 | 9.8 | 0.351 | 0.055 | 0.111 | 53 | 3.1 | 1939 | 3417 | 2103 | 32 | 46 | 85 | 6 | 15 | 25 | 85 | 16 | Yes | No | 0.8 | 574.1
REDBUD 1101 | TP7 | 18 | 79 | 13.6 | 56.8 | 9.1 | 0.638 | 0.052 | 0.1 | 57 | 2.3 | No | 3864 | 3417 | 25 | 40 | 85 | 6 | 15 | 25 | 85 | 16 | Yes | No | 2.7 | 188.6
REDBUD 1102 | TP7 | 15 | 78 | 11.6 | 48.6 | 9.6 | 0.614 | 0.055 | 0.106 | 59 | 1.5 | No | 2016 | 3864 | 34 | 46 | 82 | 3 | 27 | 38 | 85 | 11 | Yes | No | 0.4 | 636.2
RINCON 1101 | TP19 | 19 | 83 | 5.8 | 25.3 | 8.9 | 0.481 | 0.051 | 0.118 | 65 | 4.1 | No | 6165 | 2016 | 34 | 46 | 82 | 3 | 27 | 38 | 83 | 14 | Yes | No | 0.2 | 846.8
RINCON 1103 | TP19 | 18 | 78 | 5.1 | 22.9 | 9.9 | 0.412 | 0.052 | 0.117 | 65 | 3.5 | No | 1355 | 6362 | 33 | 52 | 77 | 12 | 24 | 36 | 63 | 14 | Yes | No | 0.1 | 9534.3
ROB ROY 2104 | TP18 | 20 | 70 | 12.9 | 23.5 | 14.6 | 0.355 | 0.061 | 0.123 | 64 | 16.4 | 96 | 967 | 1355 | 25 | 39 | 89 | 6 | 10 | 17 | 89 | 12 | Yes | No | 0.2 | 200.2
SILVERADO 2102 | TP7 | 21 | 84 | 18.7 | 69.5 | 8.6 | 0.672 | 0.049 | 0.112 | 61 | 6.6 | 110 | 3790 | 967 | 34 | 46 | 84 | 6 | 27 | 38 | 85 | 14 | Yes | No | 1 | 142
SILVERADO 2103 | TP19 | 24 | 82 | 10.8 | 37.4 | 8.9 | 0.565 | 0.05 | 0.109 | 64 | 2.9 | No | 2313 | 3790 | 30 | 43 | 89 | 6 | 11 | 19 | 89 | 13 | Yes | No | 0.1 | 444.9
SILVERADO 2104 | TP7 | 23 | 84 | 33.3 | 55.5 | 8.5 | 0.641 | 0.049 | 0.098 | 58 | 13.5 | 223 | No | 2313 | 34 | 46 | 84 | 3 | 27 | 38 | 85 | 14 | Yes | No | 6.6 | 34.4
SILVERADO 2105 | TP19 | 18 | 82 | 5.2 | 24.5 | 9.1 | 0.577 | 0.049 | 0.11 | 64 | 2.8 | No | 3574 | 111 | 32 | 43 | 76 | 12 | 9 | 11 | 65 | 14 | Yes | No | 0.1 | 666.3
SISQUOC 1103 | TP13 | 16 | 76 | 11 | 50.1 | 14.4 | 0.408 | 0.058 | 0.11 | 62 | 1.6 | No | 2272 | 3574 | 24 | 38 | 80 | 7 | 14 | 25 | 80 | 14 | Yes | No | 0.3 | 119.8
SONOMA 1102 | TP19 | 24 | 83 | 13.6 | 37 | 9.1 | 0.603 | 0.049 | 0.108 | 63 | 7.1 | No | 2238 | 2272 | 24 | 38 | 82 | 7 | 14 | 25 | 82 | 12 | Yes | No | 0.3 | 678
SONOMA 1103 | TP19 | 24 | 84 | 13.2 | 37.2 | 8.8 | 0.623 | 0.049 | 0.108 | 63 | 11 | No | 3196 | 2238 | 24 | 38 | 82 | 7 | 14 | 25 | 82 | 12 | Yes | No | 0.4 | 1916.9
SONOMA 1105 | TP19 | 22 | 82 | 8.3 | 55.6 | 9.2 | 0.588 | 0.049 | 0.115 | 64 | 10.6 | No | 734 | 3196 | 24 | 38 | 80 | 7 | 14 | 25 | 80 | 14 | Yes | No | 0.2 | 8389.9
SONOMA 1106 | TP19 | 18 | 84 | 6.5 | 40.9 | 8.6 | 0.58 | 0.048 | 0.115 | 64 | 6.8 | No | 1419 | 705 | 23 | 39 | 83 | 10 | 9 | 18 | 83 | 11 | Yes | No | 0 | 2646.9
STILLWATER 1101 | TP1 | 21 | 80 | 10.6 | 35.6 | 11.3 | 0.627 | 0.056 | 0.097 | 63 | 7 | 734 | 736 | 1325 | 23 | 39 | 78 | 10 | 11 | 21 | 78 | 11 | Yes | No | 2.2 | 130.6
STILLWATER 1102 | TP1 | 22 | 81 | 9.2 | 48.5 | 10.7 | 0.635 | 0.054 | 0.1 | 59 | 4.4 | 1419 | 2849 | 736 | 43 | 53 | 76 | 11 | 14 | 20 | 77 | 12 | Yes | No | 2.5 | 314.2
SUNOL 1101 | TP17 | 22 | 78 | 9.2 | 93.8 | 12.2 | 0.412 | 0.053 | 0.123 | 65 | 2.5 | 736 | 2598 | 2849 | 39 | 56 | 75 | 10 | 26 | 35 | 76 | 12 | Yes | No | 0.5 | 1114.6
TASSAJARA 2104 | TP8 | 23 | 77 | 10.5 | 127 | 12.4 | 0.465 | 0.052 | 0.122 | 64 | 4.3 | 2849 | 2204 | 2598 | 38 | 56 | 76 | 10 | 26 | 35 | 74 | 13 | Yes | No | 0.2 | 19467.2
TASSAJARA 2112 | TP8 | 28 | 77 | 15.1 | 84.5 | 11.9 | 0.537 | 0.053 | 0.12 | 61 | 11.6 | 2598 | 2666 | 2666 | 31 | 47 | 76 | 10 | 23 | 31 | 72 | 15 | Yes | No | 0.4 | 2844.7
TIDEWATER 2106 | TP8 | 23 | 77 | 9.5 | 89.7 | 12.1 | 0.344 | 0.053 | 0.109 | 59 | 3.3 | 2204 | 1851 | 1851 | 29 | 43 | 82 | 7 | 16 | 24 | 84 | 14 | Yes | No | 0.1 | 10836.7
TYLER 1105 | TP2 | 22 | 83 | 9.3 | 106 | 9.8 | 0.554 | 0.05 | 0.091 | 52 | 2.3 | 2666 | 974 | 974 | 41 | 57 | 79 | 7 | 24 | 33 | 77 | 18 | Yes | No | 2.5 | 305.1
VACA DIXON 1101 | TP6 | 25 | 83 | 8 | 62.3 | 9.3 | 0.456 | 0.048 | 0.096 | 57 | 7 | 1851 | 2355 | 2355 | 38 | 56 | 79 | 7 | 24 | 32 | 77 | 18 | Yes | No | 1.4 | 2524.6
VACA DIXON 1105 | TP6 | 23 | 83 | 6.9 | 59.2 | 9.3 | 0.285 | 0.048 | 0.097 | 58 | 6.5 | 974 | 2115 | 2116 | 25 | 41 | 79 | 7 | 13 | 18 | 75 | 19 | Yes | No | 0.1 | 55898.6
VACAVILLE 1103 | TP6 | 21 | 82 | 9 | 99.7 | 9.1 | 0.391 | 0.046 | 0.092 | 58 | 13.1 | 2355 | 2476 | 2477 | 41 | 57 | 79 | 6 | 21 | 29 | 76 | 17 | Yes | No | 0.1 | 2536.2
VACAVILLE 1104 | TP6 | 24 | 82 | 11 | 152.6 | 9.4 | 0.424 | 0.048 | 0.097 | 58 | 9.9 | 2116 | 2153 | 2153 | 41 | 57 | 79 | 7 | 24 | 33 | 79 | 14 | Yes | No | 0.4 | 2273
VACAVILLE 1108 | TP6 | 25 | 82 | 9.3 | 99.7 | 9.1 | 0.458 | 0.046 | 0.092 | 51 | 13.1 | 2477 | 2113 | 2113 | 28 | 41 | 79 | 6 | 16 | 18 | 75 | 17 | Yes | No | 1.7 | 261
VACAVILLE 1109 | TP6 | 24 | 82 | 9.9 | 134.7 | 9.1 | 0.423 | 0.047 | 0.097 | 58 | 13.3 | 2153 | 1661 | 1661 | 38 | 56 | 79 | 7 | 24 | 32 | 75 | 19 | Yes | No | 0.6 | 1470.2
VACAVILLE 1111 | TP6 | 21 | 82 | 7 | 45 | 9.1 | 0.427 | 0.047 | 0.094 | 58 | 14.2 | 2113 | 4144 | 4144 | 35 | 49 | 77 | 8 | 15 | 26 | 63 | 22 | Yes | No | 0.3 | 5261.7
VASCO 1102 | TP9 | 19 | 77 | 11 | 91.1 | 13.1 | 0.347 | 0.051 | 0.118 | 58 | 1.1 | 1661 | 1336 | 177 | 30 | 46 | 76 | 11 | 13 | 20 | 76 | 15 | Yes | No | 0.6 | 1893.6
VINEYARD 2108 | TP17 | 20 | 75 | 10.3 | 46.5 | 13 | 0.327 | 0.055 | 0.123 | 64 | 1.9 | 4144 | 1090 | 1090 | 28 | 41 | 76 | 12 | 17 | 26 | 76 | 12 | Yes | No | 0 | 1394.8
VOLTA 1101 | TP1 | 19 | 81 | 6.3 | 35.2 | 10.6 | 0.346 | 0.055 | 0.118 | 56 | 3.1 | 470 | 2246 | 2246 | 26 | 49 | 75 | 11 | 17 | 22 | 61 | 21 | Yes | No | 0 | 752.5
WESTLEY 1103 | TP9 | 26 | 78 | 11.5 | 154.3 | 13.6 | 0.327 | 0.049 | 0.094 | 55 | 3.1 | 1090 | 707 | 707 | 23 | 36 | 80 | 11 | 18 | 26 | 81 | 19 | Yes | No | 0.2 | 321.4
WILLIAMS 1102 | TP4 | 23 | 84 | 8.8 | 91.9 | 8.2 | 0.254 | 0.047 | 0.09 | 56 | 1.2 | 2246 | 328 | 122 | 25 | 34 | 77 | 13 | 14 | 20 | 78 | 20 | Yes | No | 0.1 | 431.2

## Table A-1.2
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut off Power for Each Distribution Circuit De-energized During the October 17 – 20, 2024 PSPS Event
Forecast / Agency/ Observed | Value | Name | Unit | Value Provided | Description
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
Forecast | flame_length_ft_8hr | Flame length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technosylva.
Forecast | rate_of_spread_chhr_8hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technosylva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
|  | Live Fuel Moisture Content-shrub | % |  | Live Fuel Moisture Percentage of Chamise (shrub) plant species (% of species that is comprised of water).
Forecast | lfm_chamise_new |  |  | min
Forecast | cfpd | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution.
Scaled by 1000 to convert to an integer value.
Agency | NOAA | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
Agency | RFW | Red Flag Warning | N/A | Yes/No During Event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No During Event | High Risk issued by the Federal North or South Operations Predictive Services.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed temp_f | Observed Temperature during Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
Observed | open_psps_tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
Observed | Tx_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Table A-2.1
Table A-2.1: Factors Considered in the Decision to Shut off Power for Each Transmission Circuit De-energized During the October 17 – 20, 2024 PSPS Event
Forecast | [5 empty] | Agency |  |  | Forecast | [5 empty] | Observed | [10 empty] | PSPS Risk vs. Benefit
Circuit Name | ws_mph | temp_2m_f | flame_length_ft_8hr | rate_of_spread_chhr_8hr | rh_2m | NOAA | RFW | GACC_High Risk | prob_cat | dfm_10hr | dfm_100hr | lfm_chamise_new | OA | CFPt | Observed ws_mph | Observed wg_mph | Observed temp_f | Observed RH_% | Observed ws_mph_AC | Observed wg_mph_AC | Observed temp_f_AC | Observed RH_%_AC | High Fire Risk Area (Y/N) | High Risk Vegetation Present on Circuit (Y/N) | Tx_impacts_yes_no | PSPS Potential Risk Consequence | PSPS Potential Benefit
LOWER LAKE-HOMESTAKE | 24 | 79 | 12.9 | 58.1 | 9 | No | No | No | 0.645 | 0.054 | 0.101 | 57 | 0.278 | 108.1 | 33 | 49 | 83 | 6 | 17 | 36 | 83 | 13 | Yes | Yes | No | 0 | 20664.3
ELK CREEK TAP | 24 | 84 | 11.6 | 154.5 | 8.6 | No | No | No | 0.458 | 0.048 | 0.089 | 52 | 0.009 | 2 | 26 | 37 | 87 | 5 | 14 | 23 | 87 | 16 | Yes | Yes | Yes | 0 | 1715.9
JOLON TAP | 19 | 79 | 11.3 | 76 | 12.2 | No | No | No | 0.454 | 0.055 | 0.114 | 60 | No | 0.1 | 17 | 29 | 76 | 10 | 5 | 9 | 45 | 41 | Yes | Yes | No | N/A1 | N/A2
1 The PSPS Potential Risk Consequence and PSPS Potential Benefit was not calculated for JOLON TAP circuit due to no customer impact.
2 The PSPS Potential Risk Consequence and PSPS Potential Benefit was not calculated for JOLON TAP circuit due to no customer impact.

## Table A-2.2
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut off Power for Each Transmission Circuit De-energized During the October 17 – 20, 2024 PSPS Event
Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
Forecast | flame_length_ft_8hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
Forecast | rate_of_spread_chhr_8hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
Agency | NOAA | National Oceanic and Atmospheric Administration | N/A | Yes/No during event | NOAA (SPC) Fire Weather Outlook forecast.
Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species (% of species that is comprised of water).
Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis.
Forecast | CFPt | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
Observed | Observed wg_mph | Observed Wind gust during Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
Observed | Observed temp_f | Observed Temperature during event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to All-Clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the All-Clear time.
Observed | Observed wg_mph_AC | Observed Sustained Wind gust at All Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the All-Clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear- | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the All-Clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the All-Clear time.
Observed | High Fire Risk Area | High Fire Risk Area | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through High Fire Risk Area.
Observed | High Risk Vegetation Present on Circuit | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit. PG&E does not utilize this factor in the decision to shutoff power.
Observed | transmission_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Table B-1
Table B-1. Circuits De-Energized During the October 17 – 20, 2024 PSPS Event
Distribution / Transmission | Circuit Name | De-Energization Date and Time | All-Clear Date and Time | Restoration Date and Time | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | MBL Program Customers | AFN other than MBL Program Customers | Other Customers
Distribution | ARBUCKLE 1101 | 2024-10-17 16:39 | 2024-10-19 10:09 | 2024-10-19 12:12 | COLUSA | Outside HFTD | 17 | 4 | 3 | 0 | 1 | 10
Distribution | BIG BEND 1101 | 2024-10-18 19:50 | 2024-10-19 14:23 | 2024-10-19 18:45 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 286 | 259 | 25 | 27 | 96 | 2
Distribution | BRENTWOOD 2105 | 2024-10-17 20:33 | 2024-10-19 12:00 | 2024-10-19 14:23 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 71 | 34 | 30 | 1 | 5 | 7
Distribution | BUCKS CREEK 1103 | 2024-10-18 19:55 | 2024-10-19 12:00 | 2024-10-19 16:53 | PLUMAS | Partially Outside HFTD, Tier 3, Tier 2 | 304 | 270 | 33 | 11 | 22 | 1
Distribution | CALISTOGA 1101 | 2024-10-17 18:13 | 2024-10-19 15:20 | 2024-10-19 17:42 | NAPA, SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 163 | 122 | 31 | 5 | 14 | 10
Distribution | CALISTOGA 1102 | 2024-10-17 18:20 | 2024-10-19 05:28 | 2024-10-19 09:56 | NAPA | Tier 3 | 11 | 7 | 1 | 0 | 0 | 3
Distribution | CALPINE 1144 | 2024-10-17 20:04 | 2024-10-19 14:23 | 2024-10-20 11:20 | SONOMA, LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 20 | 2 | 18 | 0 | 0 | 0
Distribution | CALPINE 1146 | 2024-10-17 20:04 | 2024-10-19 14:23 | 2024-10-20 11:20 | LAKE | Tier 3 | 1 | 0 | 1 | 0 | 0 | 0
Distribution | CANTUA 1103 | 2024-10-18 02:37 | 2024-10-19 05:28 | 2024-10-19 11:31 | FRESNO | Outside HFTD | 2 | 0 | 2 | 0 | 0 | 0
Distribution | CASTRO VALLEY 1108 | 2024-10-17 19:59 | 2024-10-19 08:53 | 2024-10-19 10:39 | ALAMEDA | Tier 3 | 78 | 61 | 14 | 2 | 5 | 3
Distribution | CAYETANO 2109 | 2024-10-17 20:39 | 2024-10-19 12:00 | 2024-10-19 14:36 | CONTRA COSTA, ALAMEDA | Tier 3, Tier 2 | 135 | 97 | 28 | 11 | 8 | 10
Distribution | CLAYTON 2212 | 2024-10-17 20:56 | 2024-10-19 13:07 | 2024-10-19 15:15 | CONTRA COSTA | Partially Outside HFTD, Tier 3, Tier 2 | 530 | 447 | 78 | 40 | 61 | 5
Distribution | CLAYTON 2213 | 2024-10-17 20:44 | 2024-10-19 05:28 | 2024-10-19 08:18 | CONTRA COSTA | Tier 2 | 4 | 0 | 4 | 0 | 0 | 0
Distribution | CLOVERDALE 1102 | 2024-10-17 18:19 | 2024-10-19 12:00 | 2024-10-19 15:04 | SONOMA, MENDOCINO | Tier 3, Tier 2 | 100 | 63 | 16 | 6 | 4 | 21
Distribution | COALINGA NO 2 1105 | 2024-10-18 02:44 | 2024-10-19 05:28 | 2024-10-19 09:57 | SAN BENITO, MONTEREY, FRESNO | Outside HFTD | 92 | 62 | 20 | 3 | 23 | 10
Distribution | CORNING 1101 | 2024-10-17 13:15 | 2024-10-18 14:55 | 2024-10-18 18:14 | TEHAMA | Partially Outside HFTD, Tier 2 | 796 | 735 | 58 | 87 | 394 | 3
Distribution | CORNING 1102 | 2024-10-17 14:10 | 2024-10-19 12:00 | 2024-10-19 15:43 | TEHAMA | Partially Outside HFTD, Tier 2 | 253 | 202 | 44 | 16 | 67 | 7
Distribution | CORTINA 1101 | 2024-10-17 16:28 | 2024-10-19 10:09 | 2024-10-19 12:28 | COLUSA | Partially Outside HFTD, Tier 2 | 17 | 6 | 10 | 0 | 1 | 1
Distribution | CRESTA 1101 | 2024-10-18 19:53 | 2024-10-19 12:00 | 2024-10-19 14:21 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 6 | 1 | 3 | 0 | 0 | 2
Distribution | DUNBAR 1101 | 2024-10-17 19:51 | 2024-10-19 08:53 | 2024-10-19 15:01 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 206 | 163 | 28 | 3 | 15 | 15
Distribution | DUNBAR 1103 | 2024-10-17 20:18 | 2024-10-19 08:53 | 2024-10-19 13:10 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 117 | 96 | 16 | 5 | 7 | 5
Distribution | DUNNIGAN 1103 | 2024-10-17 16:35 | 2024-10-19 10:09 | 2024-10-19 11:53 | YOLO, COLUSA | Partially Outside HFTD, Tier 2 | 13 | 9 | 3 | 0 | 3 | 1
Distribution | ELK CREEK 1101 | 2024-10-17 12:58 | 2024-10-19 14:23 | 2024-10-20 09:23 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 814 | 673 | 116 | 48 | 185 | 25
Distribution | FRENCH GULCH 1101 | 2024-10-17 12:59 | 2024-10-18 07:26 | 2024-10-18 10:11 | SHASTA | Tier 2 | 234 | 208 | 26 | 21 | 88 | 0
Distribution | FRENCH GULCH 1102 | 2024-10-17 12:57 | 2024-10-18 07:26 | 2024-10-18 10:24 | SHASTA | Partially Outside HFTD, Tier 2 | 37 | 10 | 26 | 1 | 1 | 1
Distribution | GEYSERVILLE 1102 | 2024-10-17 18:20 | 2024-10-19 12:00 | 2024-10-19 14:14 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 165 | 86 | 42 | 2 | 5 | 37
Distribution | GIRVAN 1101 | 2024-10-17 13:04 | 2024-10-19 05:28 | 2024-10-19 12:53 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 456 | 408 | 42 | 29 | 75 | 6
Distribution | GLENN 1101 | 2024-10-17 13:05 | 2024-10-19 12:00 | 2024-10-19 16:02 | GLENN, TEHAMA | Partially Outside HFTD, Tier 2 | 100 | 55 | 33 | 4 | 12 | 12
Distribution | HICKS 2101 | 2024-10-18 00:10 | 2024-10-19 08:53 | 2024-10-19 11:10 | SANTA CLARA | Partially Outside HFTD, Tier 3, Tier 2 | 197 | 178 | 18 | 9 | 25 | 1
Distribution | HIGHLANDS 1102 | 2024-10-17 18:23 | 2024-10-19 14:23 | 2024-10-19 16:08 | LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 28 | 23 | 5 | 2 | 11 | 0
Distribution | HIGHLANDS 1103 | 2024-10-17 18:11 | 2024-10-19 14:23 | 2024-10-19 16:40 | LAKE | Partially Outside HFTD, Tier 2 | 49 | 34 | 11 | 5 | 9 | 4
Distribution | JAMESON 1102 | 2024-10-17 17:45 | 2024-10-19 05:28 | 2024-10-19 09:52 | SOLANO | Tier 2 | 32 | 29 | 3 | 1 | 4 | 0
Distribution | JAMESON 1105 | 2024-10-17 17:13 | 2024-10-19 05:28 | 2024-10-19 10:23 | SOLANO | Tier 2 | 5 | 2 | 3 | 0 | 0 | 0
Distribution | JOLON 1102 | 2024-10-18 02:46 | 2024-10-19 05:28 | 2024-10-19 13:06 | MONTEREY | Partially Outside HFTD, Tier 2 | 570 | 418 | 92 | 21 | 90 | 60
Distribution | JOLON 1103 | 2024-10-18 02:31 | 2024-10-19 05:28 | 2024-10-19 11:36 | MONTEREY | Partially Outside HFTD, Tier 2 | 18 | 0 | 18 | 0 | 0 | 0
Distribution | KESWICK 1101 | 2024-10-17 13:03 | 2024-10-19 05:28 | 2024-10-19 11:25 | SHASTA | Tier 3, Tier 2 | 320 | 250 | 69 | 14 | 79 | 1
Distribution | LAKEVILLE 1102 | 2024-10-17 19:48 | 2024-10-18 07:26 | 2024-10-18 09:46 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 22 | 10 | 7 | 1 | 1 | 5
Distribution | LOGAN CREEK 2102 | 2024-10-17 13:08 | 2024-10-19 14:23 | 2024-10-19 17:59 | GLENN | Partially Outside HFTD, Tier 2 | 77 | 33 | 28 | 0 | 0 | 16
Distribution | LONE TREE 2105 | 2024-10-17 20:31 | 2024-10-19 12:00 | 2024-10-19 12:50 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 70 | 56 | 10 | 1 | 13 | 4
Distribution | LOS GATOS 1107 | 2024-10-18 00:08 | 2024-10-19 12:00 | 2024-10-19 14:53 | SANTA CLARA, SANTA CRUZ | Partially Outside HFTD, Tier 3 | 179 | 142 | 36 | 10 | 17 | 1
Distribution | MADISON 1105 | 2024-10-17 17:29 | 2024-10-19 10:09 | 2024-10-19 13:15 | YOLO | Partially Outside HFTD, Tier 2 | 6 | 3 | 2 | 1 | 0 | 1
Distribution | MADISON 2101 | 2024-10-17 17:33 | 2024-10-19 10:09 | 2024-10-19 14:09 | YOLO | Partially Outside HFTD, Tier 2 | 19 | 3 | 13 | 0 | 0 | 3
Distribution | MAXWELL 1102 | 2024-10-17 16:32 | 2024-10-19 10:09 | 2024-10-19 12:33 | COLUSA | Outside HFTD | 11 | 5 | 2 | 0 | 0 | 4
Distribution | MAXWELL 1105 | 2024-10-17 16:22 | 2024-10-19 14:23 | 2024-10-19 15:53 | COLUSA | Partially Outside HFTD, Tier 2 | 54 | 27 | 18 | 0 | 2 | 9
Distribution | MIDDLETOWN 1101 | 2024-10-17 18:17 | 2024-10-19 14:23 | 2024-10-19 18:47 | NAPA, SONOMA, LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 378 | 333 | 40 | 14 | 96 | 5
Distribution | MILPITAS 1109 | 2024-10-17 19:47 | 2024-10-19 12:00 | 2024-10-19 17:39 | SANTA CLARA, ALAMEDA | Partially Outside HFTD, Tier 2 | 183 | 144 | 34 | 12 | 24 | 5
Distribution | MONTICELLO 1101 | 2024-10-17 17:13 | 2024-10-19 12:00 | 2024-10-19 16:08 | NAPA, SOLANO | Partially Outside HFTD, Tier 3, Tier 2 | 487 | 395 | 58 | 23 | 58 | 34
Distribution | MORGAN HILL 2111 | 2024-10-18 00:18 | 2024-10-19 08:53 | 2024-10-19 13:33 | SANTA CLARA | Tier 3, Tier 2 | 167 | 147 | 18 | 15 | 13 | 2
Distribution | NAPA 1112 | 2024-10-17 17:29 | 2024-10-19 05:28 | 2024-10-19 09:27 | NAPA | Tier 2 | 5 | 4 | 0 | 3 | 0 | 1
Distribution | NORTH DUBLIN 2103 | 2024-10-17 20:41 | 2024-10-19 12:00 | 2024-10-19 14:30 | CONTRA COSTA, ALAMEDA | Partially Outside HFTD, Tier 2 | 63 | 54 | 7 | 4 | 8 | 2
Distribution | ORO FINO 1102 | 2024-10-18 19:52 | 2024-10-19 08:53 | 2024-10-19 17:22 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 809 | 754 | 51 | 51 | 182 | 4
Distribution | PANOCHE 1103 | 2024-10-18 02:55 | 2024-10-19 05:28 | 2024-10-19 09:13 | SAN BENITO | Partially Outside HFTD, Tier 2 | 23 | 7 | 16 | 0 | 0 | 0
Distribution | PARADISE 1105 | 2024-10-18 20:02 | 2024-10-19 08:53 | 2024-10-19 13:01 | BUTTE | Tier 3 | 50 | 48 | 2 | 9 | 9 | 0
Distribution | PUEBLO 1104 | 2024-10-17 18:18 | 2024-10-19 12:00 | 2024-10-19 13:19 | NAPA | Tier 2 | 37 | 25 | 6 | 3 | 7 | 6
Distribution | PUEBLO 1105 | 2024-10-17 18:21 | 2024-10-19 12:00 | 2024-10-19 14:23 | NAPA | Partially Outside HFTD, Tier 2 | 96 | 63 | 18 | 0 | 10 | 15
Distribution | PUEBLO 2102 | 2024-10-17 19:39 | 2024-10-19 08:53 | 2024-10-19 13:12 | NAPA, SONOMA | Partially Outside HFTD, Tier 3 | 80 | 64 | 14 | 3 | 9 | 2
Distribution | PUEBLO 2103 | 2024-10-17 19:42 | 2024-10-19 08:53 | 2024-10-19 16:23 | NAPA | Partially Outside HFTD, Tier 3, Tier 2 | 263 | 189 | 38 | 6 | 16 | 36
Distribution | PUTAH CREEK 1102 | 2024-10-17 17:14 | 2024-10-19 10:09 | 2024-10-19 16:25 | YOLO, SOLANO | Partially Outside HFTD, Tier 2 | 258 | 186 | 46 | 16 | 18 | 26
Distribution | PUTAH CREEK 1103 | 2024-10-17 17:17 | 2024-10-19 13:07 | 2024-10-19 15:28 | YOLO, SOLANO | Partially Outside HFTD, Tier 2 | 52 | 47 | 1 | 4 | 6 | 4
Distribution | PUTAH CREEK 1105 | 2024-10-17 17:36 | 2024-10-19 10:09 | 2024-10-19 12:28 | YOLO | Partially Outside HFTD, Tier 2 | 36 | 19 | 7 | 4 | 0 | 10
Distribution | RAWSON 1103 | 2024-10-17 13:15 | 2024-10-18 14:55 | 2024-10-18 17:03 | TEHAMA | Partially Outside HFTD, Tier 2 | 9 | 4 | 4 | 0 | 0 | 1
Distribution | RED BLUFF 1101 | 2024-10-17 13:51 | 2024-10-18 14:55 | 2024-10-18 17:44 | TEHAMA | Partially Outside HFTD, Tier 2 | 67 | 67 | 0 | 7 | 22 | 0
Distribution | RED BLUFF 1103 | 2024-10-17 13:53 | 2024-10-18 14:55 | 2024-10-18 18:14 | TEHAMA | Partially Outside HFTD, Tier 2 | 160 | 152 | 7 | 14 | 28 | 1
Distribution | RED BLUFF 1105 | 2024-10-17 13:07 | 2024-10-18 14:55 | 2024-10-18 17:00 | TEHAMA | Partially Outside HFTD, Tier 2 | 233 | 219 | 8 | 24 | 48 | 6
Distribution | REDBUD 1101 | 2024-10-17 18:25 | 2024-10-19 14:23 | 2024-10-19 18:09 | LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 541 | 497 | 31 | 53 | 195 | 13
Distribution | REDBUD 1102 | 2024-10-17 18:18 | 2024-10-19 13:07 | 2024-10-19 14:30 | LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 48 | 37 | 2 | 5 | 16 | 9
Distribution | RINCON 1101 | 2024-10-17 19:58 | 2024-10-19 08:53 | 2024-10-19 11:15 | SONOMA | Partially Outside HFTD, Tier 3 | 47 | 35 | 11 | 4 | 8 | 1
Distribution | RINCON 1103 | 2024-10-17 20:03 | 2024-10-19 08:53 | 2024-10-19 12:03 | SONOMA | Partially Outside HFTD, Tier 3 | 12 | 10 | 2 | 0 | 0 | 0
Distribution | ROB ROY 2104 | 2024-10-18 00:17 | 2024-10-19 08:53 | 2024-10-19 12:24 | SANTA CRUZ | Partially Outside HFTD, Tier 3 | 88 | 77 | 10 | 4 | 13 | 1
Distribution | SILVERADO 2102 | 2024-10-17 18:15 | 2024-10-19 12:00 | 2024-10-19 17:30 | NAPA | Partially Outside HFTD, Tier 3, Tier 2 | 325 | 184 | 70 | 4 | 15 | 71
Distribution | SILVERADO 2103 | 2024-10-17 20:34 | 2024-10-19 08:53 | 2024-10-19 11:16 | NAPA, SONOMA | Tier 3 | 14 | 9 | 3 | 0 | 0 | 2
Distribution | SILVERADO 2104 | 2024-10-17 18:30 | 2024-10-19 12:00 | 2024-10-20 13:18 | NAPA | Partially Outside HFTD, Tier 3, Tier 1, Tier 2 | 1589 | 1337 | 137 | 86 | 234 | 115
Distribution | SILVERADO 2105 | 2024-10-17 19:42 | 2024-10-19 08:53 | 2024-10-19 14:04 | NAPA, SONOMA | Tier 3 | 22 | 12 | 4 | 0 | 0 | 6
Distribution | SISQUOC 1103 | 2024-10-18 08:25 | 2024-10-19 08:53 | 2024-10-19 11:00 | SANTA BARBARA | Partially Outside HFTD, Tier 3, Tier 2 | 155 | 120 | 24 | 4 | 15 | 11
Distribution | SONOMA 1102 | 2024-10-17 19:46 | 2024-10-19 08:53 | 2024-10-19 11:20 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 108 | 94 | 7 | 1 | 12 | 7
Distribution | SONOMA 1103 | 2024-10-17 19:52 | 2024-10-19 08:53 | 2024-10-19 11:31 | SONOMA | Partially Outside HFTD, Tier 3 | 131 | 115 | 5 | 5 | 9 | 11
Distribution | SONOMA 1105 | 2024-10-17 20:30 | 2024-10-19 08:53 | 2024-10-19 12:42 | NAPA, SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 74 | 65 | 5 | 1 | 4 | 4
Distribution | SONOMA 1106 | 2024-10-17 19:49 | 2024-10-19 08:53 | 2024-10-19 11:02 | SONOMA | Tier 3 | 8 | 3 | 5 | 0 | 0 | 0
Distribution | STILLWATER 1101 | 2024-10-17 13:19 | 2024-10-19 10:09 | 2024-10-19 13:36 | SHASTA | Partially Outside HFTD, Tier 2 | 606 | 537 | 63 | 59 | 197 | 6
Distribution | STILLWATER 1102 | 2024-10-17 13:27 | 2024-10-19 10:09 | 2024-10-19 12:34 | SHASTA | Partially Outside HFTD, Tier 2 | 724 | 702 | 22 | 70 | 216 | 0
Distribution | SUNOL 1101 | 2024-10-17 20:04 | 2024-10-19 12:00 | 2024-10-19 17:43 | ALAMEDA | Partially Outside HFTD, Tier 1, Tier 3, Tier 2 | 74 | 51 | 20 | 4 | 3 | 3
Distribution | TASSAJARA 2104 | 2024-10-17 20:39 | 2024-10-19 12:00 | 2024-10-19 14:00 | CONTRA COSTA, ALAMEDA | Partially Outside HFTD, Tier 3, Tier 2 | 59 | 48 | 9 | 2 | 5 | 2
Distribution | TASSAJARA 2112 | 2024-10-17 21:02 | 2024-10-19 13:07 | 2024-10-19 14:53 | CONTRA COSTA | Tier 3 | 27 | 15 | 12 | 1 | 1 | 0
Distribution | TIDEWATER 2106 | 2024-10-17 20:35 | 2024-10-19 05:28 | 2024-10-19 08:32 | CONTRA COSTA | Tier 2 | 25 | 15 | 9 | 0 | 1 | 1
Distribution | TYLER 1105 | 2024-10-17 13:03 | 2024-10-18 14:55 | 2024-10-18 17:48 | TEHAMA | Partially Outside HFTD, Tier 2 | 495 | 425 | 41 | 50 | 123 | 29
Distribution | VACA DIXON 1101 | 2024-10-17 17:21 | 2024-10-19 13:07 | 2024-10-19 17:23 | SOLANO | Partially Outside HFTD, Tier 2 | 505 | 473 | 31 | 49 | 64 | 1
Distribution | VACA DIXON 1105 | 2024-10-17 17:32 | 2024-10-19 13:07 | 2024-10-19 15:20 | SOLANO | Partially Outside HFTD, Tier 2 | 27 | 24 | 0 | 3 | 8 | 3
Distribution | VACAVILLE 1103 | 2024-10-17 17:40 | 2024-10-19 05:28 | 2024-10-19 08:54 | SOLANO | Partially Outside HFTD, Tier 2 | 37 | 35 | 2 | 4 | 3 | 0
Distribution | VACAVILLE 1104 | 2024-10-17 17:22 | 2024-10-19 05:28 | 2024-10-19 12:00 | SOLANO | Partially Outside HFTD, Tier 2 | 150 | 115 | 28 | 11 | 23 | 7
Distribution | VACAVILLE 1108 | 2024-10-17 17:22 | 2024-10-19 13:07 | 2024-10-19 18:42 | NAPA, SOLANO | Partially Outside HFTD, Tier 2 | 813 | 724 | 67 | 69 | 59 | 22
Distribution | VACAVILLE 1109 | 2024-10-17 17:26 | 2024-10-19 05:28 | 2024-10-19 10:27 | SOLANO | Partially Outside HFTD, Tier 2 | 161 | 149 | 11 | 24 | 36 | 1
Distribution | VACAVILLE 1111 | 2024-10-17 17:24 | 2024-10-19 13:07 | 2024-10-19 15:37 | SOLANO | Partially Outside HFTD, Tier 2 | 88 | 83 | 5 | 8 | 10 | 0
Distribution | VASCO 1102 | 2024-10-17 21:20 | 2024-10-19 10:09 | 2024-10-19 15:40 | ALAMEDA | Partially Outside HFTD, Tier 2 | 217 | 153 | 50 | 16 | 21 | 14
Distribution | VINEYARD 2108 | 2024-10-17 19:48 | 2024-10-19 05:28 | 2024-10-19 07:44 | ALAMEDA | Tier 3 | 6 | 2 | 2 | 0 | 0 | 2
Distribution | VOLTA 1101 | 2024-10-17 13:01 | 2024-10-19 08:53 | 2024-10-19 10:54 | TEHAMA | Partially Outside HFTD, Tier 2 | 7 | 0 | 6 | 0 | 0 | 1
Distribution | WESTLEY 1103 | 2024-10-17 21:17 | 2024-10-19 10:09 | 2024-10-19 11:55 | STANISLAUS | Outside HFTD | 26 | 3 | 21 | 0 | 0 | 2
Distribution | WILLIAMS 1102 | 2024-10-17 16:38 | 2024-10-19 10:09 | 2024-10-19 12:47 | COLUSA | Outside HFTD | 15 | 7 | 5 | 0 | 2 | 3
Transmission | Elk Creek Tap | 2024-10-17 13:22 | 2024-10-19 14:23 | 2024-10-19 16:04 | Transmission Line | Partially Outside HFTD, Tier 2 | 1 1 | 0 | 0 | 0 | 0 | 0
Transmission | Lower Lake-Homestake* | 2024-10-17 18:09 | 2024-10-19 14:23 | 2024-10-19 16:26 | Transmission Line | Tier 1 & Tier 2 | 1 | 0 | 0 | 0 | 0 | 0
Transmission | Jolon Tap | 2024-10-18 03:19 | 2024-10-19 05:28 | 2024-10-19 09:59 | Transmission Line | Tier 1 & Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
Total | [6 empty] | 17367 | 14370 | 2181 | 1136 | 3190 | 814
1 Foreign Line de-energized with Elk Creek Tap per TOTL WC T24-016269

## Table C-1
Table C-1. Damages & Hazards Found Within the De-Energized Areas
Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage/ Hazard | Type of Damage/Hazard | Description of Damage
Silverado 2104 | Napa | 102253166 | Non-HFTD | Damage | Vegetation | Broken conductor
Rob Roy 2104 | Santa Cruz | 101682184 | Tier 3 | Damage | Wind Related | Broken tie wire
Rob Roy 2104 | Santa Cruz | 103998482 | Tier 3 | Hazard | Vegetation | Tree branch on line

## Table D-1
Table D-1. Public Safety Partners Contacted
Organization/Jurisdiction | Title | HFTD or HFRA Tier1 | Date/Time Contacted (PDT)
Alameda County | Board President | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Board Vice President | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | County Administrator | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | County Clerk Recorder | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Division Chief | Tier 3, Tier 2 | 10/15/2024 07:23 PDT
Alameda County | Division Chief of Operations/ Emergency Management | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | EMS Disaster and WMD Coordinator | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Emergency Preparedness Manager | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Fire Chief | Tier 3, Tier 2 | 10/15/2024 07:23 PDT
Alameda County | General | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Main Line | Tier 3, Tier 2 | 10/15/2024 07:23 PDT
Alameda County | OES Capt | Tier 3, Tier 2 | 10/15/2024 07:21 PDT
Alameda County | OES EOC Lead | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | President of the Board | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Safety & Emergency Preparedness Manager | Tier 3, Tier 2 | 10/15/2024 07:21 PDT
Alameda County | Senior Emergency Services Coordinator | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Sheriff | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Superintendent of Water Distribution | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Supervisor | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Technician | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County | Train Ops | Tier 3, Tier 2 | 10/15/2024 07:23 PDT
Alameda County | Watch Commander | Tier 3, Tier 2 | 10/15/2024 07:23 PDT
Alameda County | Water Operations Manager | Tier 3, Tier 2 | 10/15/2024 07:22 PDT
Alameda County CCA | General | Tier 3, Tier 2 | 10/15/2024 07:21 PDT
Alameda County Communication Facility | American Tower Corporation | Tier 3 | 10/17/2024 04:12 PDT
Alameda County Communication Facility | AT&T Services Inc | Tier 2 | 10/16/2024 08:07 PDT
Alameda County Communication Facility | Global Valley Networks | Tier 2 | 10/15/2024 07:13 PDT
Alameda County Communication Facility | Verizon Wireless | Tier 2 | 10/16/2024 08:07 PDT
Alameda County Fremont | City Clerk | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | City Leadership | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | City Manager | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Council Member | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Deputy Chief | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Deputy Chief of Police | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Emergency Services Manager | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Fire Chief | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | General | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Mayor | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | OES Duty officer | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Police Chief | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Police Watch Commander | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Public Works Director | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Fremont | Vice Mayor | Tier 1, Tier 2 | 10/17/2024 16:45 PDT
Alameda County Hayward | City Clerk | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | City Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Council Member | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Fire Chief | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Mayor | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Mayor Pro Tem | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Police Chief | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Hayward | Utilities Operations & Maintenance Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Other Facility | City and County of San Francisco | Tier 2 | 10/16/2024 08:07 PDT
Alameda County Other Facility | County of Alameda | Tier 2 | 10/16/2024 08:07 PDT
Alameda County Other Facility | Gexpro | Tier 2 | 10/16/2024 08:07 PDT
Alameda County Pleasanton | Assistant City Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Assistant to the City Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | City Clerk | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | City Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | City Traffic Engineer | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Council Member | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Director of Engineering | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Director of Information Technology | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Director of Library and Recreation | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Director of Operations and Water Utilities | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Emergency Preparedness Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Fire Chief | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Mayor | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Non-Emergency | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Police Chief | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Public Information officer | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Training and Emergency Services Manager | Tier 3 | 10/17/2024 16:45 PDT
Alameda County Pleasanton | Vice Mayor | Tier 3 | 10/17/2024 16:45 PDT
Alpine County | Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | County Administrative officer | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Alpine County | County Clerk | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | Dispatch | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Alpine County | General | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Alpine County | Health officer | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | Sheriff | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | Supervisor | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | Under Sheriff | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County | Vice Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Alpine County Communication Facility | AT&T Services Inc | Tier 1 | 10/15/2024 07:13 PDT
Alpine County Communication Facility | New Cingular Wireless LLC | HFRA | 10/15/2024 07:05 PDT
Alpine County Emergency Services Facility | County of Alpine | Tier 1 | 10/15/2024 07:13 PDT
Alpine County Other Facility | Skyline Bear Valley Resorts Inc | HFRA | 10/15/2024 07:05 PDT
Alpine County Water and Waste Water Facility | Bear Valley Water District | HFRA | 10/15/2024 07:05 PDT
Alpine County Water and Waste Water Facility | Lake Alpine Water Co | HFRA | 10/15/2024 07:05 PDT
Amador County | Board member District 1 | Tier 2 | 10/15/2024 07:22 PDT
Amador County | County Administrative officer | Tier 2 | 10/15/2024 07:22 PDT
Amador County | County Clerk/Recorder | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Director | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Division Chief | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Fire Chief | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Health officer | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Lieutenant, Dispatch/OES | Tier 2 | 10/15/2024 07:22 PDT
Amador County | OES Coordinator / Sergeant | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Police Chief | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Program Manager for Emergency Preparedness | Tier 2 | 10/15/2024 07:23 PDT
Amador County | Supervisor | Tier 2 | 10/15/2024 07:22 PDT
Amador County | Supervisor District 3 | Tier 2 | 10/15/2024 07:22 PDT
Amador County Communication Facility | Volcano Telephone | Tier 2 | 10/15/2024 07:13 PDT
Amador County Other Facility | Pacific Gas & Electric Company | Tier 2 | 10/15/2024 07:05 PDT
Butte County | Admin Analyst II | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Butte County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Chief Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | County Clerk-Recorder | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Deputy Chief | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Butte County | Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Division Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | General Services Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Interim OEM Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Lieutenant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Public Health Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Sergeant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County | Vice Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Chico | Captain | Tier 2 | 10/16/2024 07:59 PDT
Butte County Chico | City Clerk | Tier 2 | 10/16/2024 17:55 PDT
Butte County Chico | City Manager | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Council Member | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Deputy Chief | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Fire Chief | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Mayor | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Police Chief | Tier 2 | 10/16/2024 08:00 PDT
Butte County Chico | Vice Mayor | Tier 2 | 10/16/2024 07:59 PDT
Butte County Communication Facility | AT&T Mobility | Tier 3 | 10/15/2024 07:05 PDT
Butte County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Butte County Communication Facility | California Department of Forestry | Tier 3 | 10/16/2024 08:07 PDT
Butte County Emergency Services Facility | California Department of Forestry | Tier 3 | 10/15/2024 07:05 PDT
Butte County Emergency Services Facility | County of Butte | Tier 3 | 10/15/2024 07:05 PDT
Butte County Oroville | Assistant City Clerk | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | City Administrator | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Council Member | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Deputy Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Division Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Police Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Oroville | Vice Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Butte County Other Facility | California Department of Forestry | Tier 3 | 10/15/2024 07:05 PDT
Calaveras County | Board Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Board Vice Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | County Clerk/Recorder | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Emergency Services Coordinator | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Fire Chief | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Health officer | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Interim County Administrative officer | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Interim Emergency Services Coordinator | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Interim Emergency Services Director | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Local Cal Fire | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Calaveras County | Sheriff | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Calaveras County | Supervisor | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Calaveras County Communication Facility | AT&T Services Inc | Tier 3 | 10/15/2024 07:04 PDT
Calaveras County Communication Facility | Comcast Fresno LLC | Tier 3 | 10/15/2024 07:04 PDT
Calaveras County Communication Facility | Media One Inc | Tier 3 | 10/15/2024 07:05 PDT
Calaveras County Communication Facility | Verizon | Tier 3 | 10/15/2024 07:05 PDT
Calaveras County Other Facility | Us Department of Agriculture | Tier 3 | 10/15/2024 07:05 PDT
Colusa County | Board Chair | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | County Clerk/Recorder | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | County Supervisor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Deputy Chief | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Director | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Division Chief | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Emergency Service Technician | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Fire Chief | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | General | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | MHOAC | HFRA, Tier 2 | 10/15/2024 07:23 PDT
Colusa County | Sheriff | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Supervisor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County | Vice Chair | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County Communication Facility | AT&T | Tier 2 | 10/15/2024 07:13 PDT
Colusa County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:04 PDT
Colusa County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:04 PDT
Colusa County Communication Facility | Citizens Telecommunications of California Inc. | Tier 2 | 10/15/2024 07:05 PDT
Colusa County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 10/15/2024 07:04 PDT
Colusa County Communication Facility | Gte Mobile Net of California Lp | Tier 2 | 10/15/2024 07:05 PDT
Colusa County Emergency Services Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Colusa County Emergency Services Facility | County of Colusa | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Colusa County Emergency Services Facility | Indian Valley - Bear Valley Fire Protection Distri | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:13 PDT
Colusa County Emergency Services Facility | Indian Valley Fire Protection District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:13 PDT
Colusa County Energy Sector Facility | City of Santa Clara | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:04 PDT
Colusa County Energy Sector Facility | Western Area Power Administration | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Colusa County Tribal | Chairperson | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Colusa County Water And Waste Water Facility | California Department Of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Colusa County Water and Waste Water Facility | County Of Colusa | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Board Vice Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Chair of the Board | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Chief of Staff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | County Administrator | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Contra Costa County | County Clerk Recorder | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Deputy Fire Chief, Mutual Aid Coordinator | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Contra Costa County | Duty officer | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Contra Costa County | Duty officer - 24/7 Staff call line | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Emergency Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Emergency Preparedness Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | OES Warning System | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Antioch | City Clerk | Tier 2 | 10/16/2024 17:55 PDT
Contra Costa County Antioch | City Manager | Tier 2 | 10/16/2024 08:00 PDT
Contra Costa County Antioch | Council Member | Tier 2 | 10/16/2024 17:55 PDT
Contra Costa County Antioch | Emergency | Tier 2 | 10/16/2024 08:00 PDT
Contra Costa County Antioch | Mayor | Tier 2 | 10/16/2024 17:55 PDT
Contra Costa County Antioch | Mayor Pro Tem | Tier 2 | 10/16/2024 17:55 PDT
Contra Costa County Antioch | Police Chief | Tier 2 | 10/16/2024 08:00 PDT
Contra Costa County CCA | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | City Clerk | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | City Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | Council Member | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | Interim City Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Clayton | Non-Emergency | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Contra Costa County Clayton | Police Chief | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Contra Costa County Clayton | Vice Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Contra Costa County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:04 PDT
Contra Costa County Communication Facility | AT&T Pacific Bell | Tier 2 | 10/15/2024 07:13 PDT
Contra Costa County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | County of Contra Costa | Tier 3 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | GTE Mobile Net of California LP | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Contra Costa County Communication Facility | SBA Towers | Tier 2 | 10/15/2024 07:13 PDT
Contra Costa County Communication Facility | Sprint Corporation | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | T-Mobile West Corporation | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | T-Mobile West LLC | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | US Coast Guard | Tier 3 | 10/15/2024 07:05 PDT
Contra Costa County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:13 PDT
Contra Costa County Communication Facility | Verizon Wireless | Tier 2 | 10/16/2024 08:07 PDT
Contra Costa County Emergency Services Facility | California Department of Forestry | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Emergency Services Facility | County of Contra Costa | Tier 3 | 10/15/2024 07:05 PDT
Contra Costa County Emergency Services Facility | San Ramon Valley Fire District | Tier 3 | 10/15/2024 07:05 PDT
Contra Costa County Government - Jail Facility | County of Contra Costa | Tier 3, Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Other Facility | Contra Costa Water District | Tier 2 | 10/15/2024 07:05 PDT
Contra Costa County Pittsburg | Chief of Police | Tier 2 | 10/15/2024 07:22 PDT
Contra Costa County Pittsburg | City Clerk | Tier 2 | 10/15/2024 07:21 PDT
Contra Costa County Pittsburg | City Manager | Tier 2 | 10/15/2024 07:22 PDT
Contra Costa County Pittsburg | Council Member | Tier 2 | 10/15/2024 07:21 PDT
Contra Costa County Pittsburg | Emergency | Tier 2 | 10/15/2024 07:23 PDT
Contra Costa County Pittsburg | Fire Chief | Tier 2 | 10/15/2024 07:23 PDT
Contra Costa County Pittsburg | Mayor | Tier 2 | 10/15/2024 07:22 PDT
Contra Costa County Pittsburg | Non-Emergency | Tier 2 | 10/15/2024 07:23 PDT
Contra Costa County Pittsburg | Vice Mayor | Tier 2 | 10/15/2024 07:22 PDT
El Dorado County | Battalion Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Board Chair / District III Supervisor | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Board First Vice Chair | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Board Second Vice Chair | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Chief Administrative officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Commander | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | County Clerk-Recorder | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Fire Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Interim Fire Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Local Cal Fire | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Medical Health Operational Area Coordinator | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | MHOAC | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | OES Deputy | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | OES Sergeant | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | OES/Sheriff | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Sheriff | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Supervisor | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Supervisor District 4 | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County | Wildfire Preparedness/ Resilience officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
El Dorado County CCA | General | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
El Dorado County Communication Facility | American Tower Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:04 PDT
El Dorado County Communication Facility | AT&T Services Inc | Tier 1 | 10/15/2024 07:04 PDT
El Dorado County Communication Facility | Crown Castle International | Tier 2 | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | Newpath Networks LLC | Tier 1, Tier 2 | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | Sprint Nextel Corporation | Tier 2 | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | T-Mobile | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:13 PDT
El Dorado County Communication Facility | T-Mobile West Corporation | Tier 2 | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
El Dorado County Communication Facility | Verizon Wireless Services LLC | Tier 1 | 10/15/2024 07:13 PDT
El Dorado County Emergency Services Facility | El Dorado County Fire Dept | Tier 1 | 10/15/2024 07:05 PDT
El Dorado County Other Facility | Sprint Nextel Corporation | Tier 2 | 10/15/2024 07:05 PDT
El Dorado County Water and Waste Water Facility | El Dorado Irrigation District | Tier 1 | 10/15/2024 07:05 PDT
Fresno County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Chair of the Board | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | City Clerk | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Fresno County | County Clerk | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | City Manager | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Fresno County | Council Member | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | County Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Emergency | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Fresno County | Emergency Management Specialist | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Facility Services | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Lieutenant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | MHOAC | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Mayor Pro Tem | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | OES Director of Emergency Services | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Staff Analyst | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Communication Facility | American Tower Corporation | HFRA | 10/16/2024 08:07 PDT
Fresno County Communication Facility | AT&T Services Inc | HFRA | 10/16/2024 08:07 PDT
Fresno County Communication Facility | Crown Castle International | Tier 2 | 10/15/2024 07:05 PDT
Fresno County Communication Facility | Pinnacle Towers Inc | HFRA | 10/16/2024 08:07 PDT
Fresno County Communication Facility | Ponderosa Telephone Co | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Fresno County Communication Facility | T-Mobile USA Inc | Tier 2 | 10/15/2024 07:05 PDT
Fresno County Communication Facility | USA Media Group | Tier 3 | 10/15/2024 07:05 PDT
Fresno County Emergency Services Facility | Bald Mountain Fire Protection District | Tier 2 | 10/15/2024 07:13 PDT
Fresno County Other Facility | Dean, Allan | Tier 2 | 10/15/2024 07:13 PDT
Fresno County Tribal | Chairperson | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Environmental Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Housing Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | MWC GM | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Member at Large | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Secretary | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Treasurer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Tribal Administrator | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Fresno County Tribal | Vice Chairperson | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Glenn County | CAO | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | County Administrative officer | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | Deputy Director OES | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | Director of Public Works Agency | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | Fire Chief | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | General | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County | Sheriff | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County Communication Facility | American Tower Corporation | Tier 2 | 10/15/2024 07:05 PDT
Glenn County Communication Facility | AT&T Services Inc | HFRA, Tier 2 | 10/15/2024 07:04 PDT
Glenn County Communication Facility | GTE Mobile Net of California LP | HFRA | 10/15/2024 07:05 PDT
Glenn County Communication Facility | Verizon | Tier 2 | 10/15/2024 07:05 PDT
Glenn County Emergency Services Facility | County of Glenn | Tier 2 | 10/15/2024 07:05 PDT
Glenn County Emergency Services Facility | Elk Creek Fire District | Tier 2 | 10/15/2024 07:05 PDT
Glenn County Energy Sector Facility | City of Santa Clara | HFRA | 10/15/2024 07:04 PDT
Glenn County Orland | City Clerk | HFRA | 10/15/2024 07:22 PDT
Glenn County Orland | City Manager | HFRA | 10/15/2024 07:22 PDT
Glenn County Orland | Fire Chief | HFRA | 10/15/2024 07:22 PDT
Glenn County Orland | General | HFRA | 10/15/2024 07:23 PDT
Glenn County Orland | Public Works Director | HFRA | 10/15/2024 07:22 PDT
Glenn County Other Facility | US Army Corps of Engineers | HFRA | 10/15/2024 07:05 PDT
Glenn County Tribal | Interim Tribal Secretary | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County Tribal | Tribal Administrator | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Glenn County Water and Waste Water Facility | Elk Creek Community Service | Tier 2 | 10/15/2024 07:05 PDT
Glenn County Water and Waste Water Facility | US Army Corps of Engineers | HFRA | 10/15/2024 07:05 PDT
Lake County | Battalion Chief | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Lake County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Chair of the Board | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | City Manager | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Lake County | Council Member | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | County Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | County Supervisor, District 4 | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Dispatch | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | District 3 County Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | District 5 Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | District Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Emergency Services Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Health Services Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Lieutenant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Mayor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Lake County Clearlake | City Manager | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Clearlake | Council Member | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Clearlake | Councilman | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Clearlake | Lieutenant - Operations | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Clearlake | Non-Emergency | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:20 PDT
Lake County Clearlake | Police Chief | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Clearlake | Vice Mayor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/17/2024 14:19 PDT
Lake County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:05 PDT
Lake County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Lake County Communication Facility | Mediacom California LLC | Tier 2 | 10/15/2024 07:05 PDT
Lake County Communication Facility | Verizon Wireless | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/16/2024 08:07 PDT
Lake County Communication Facility | Williams Communication LLC | Tier 2 | 10/17/2024 04:12 PDT
Lake County Emergency Services Facility | Northshore Fire Protection District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/16/2024 08:07 PDT
Lake County Tribal | Chairman | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Cultural Resources | Tier 2, Tier 3 | 10/19/2024 12:31 PDT
Lake County Tribal | Environmental Director | Tier 2, Tier 3 | 10/19/2024 12:31 PDT
Lake County Tribal | Representative | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Secretary | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Treasurer | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Tribal Administrator | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Vice Chairman | Tier 2, Tier 3 | 10/17/2024 14:19 PDT
Lake County Tribal | Vice Chairperson | Tier 2, Tier 3 | 10/19/2024 12:31 PDT
Madera County | CAO | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Cal FIRE Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Command Center | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Madera County | Command Staff E-Mail | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | County Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | County Clerk | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Madera County | Dispatch | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Emergency Command Center | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Madera County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Lieutenant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | MHOAC | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | OES Coordinator | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | OES Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Sergeant | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County | Unit Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Communication Facility | County of Madera | Tier 3 | 10/15/2024 07:05 PDT
Madera County Communication Facility | Northland Cable Television Inc | Tier 3 | 10/15/2024 07:04 PDT
Madera County Communication Facility | Ponderosa Telephone Co | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Madera County Communication Facility | Sierra Telephone Company Inc | Tier 3 | 10/15/2024 07:05 PDT
Madera County Communication Facility | T-Mobile West Corporation | Tier 3 | 10/15/2024 07:05 PDT
Madera County Communication Facility | Verizon | Tier 3 | 10/15/2024 07:13 PDT
Madera County Emergency Services Facility | County of Madera | Tier 2 | 10/15/2024 07:04 PDT
Madera County Other Facility | Dept of Forestry | Tier 3 | 10/15/2024 07:13 PDT
Madera County Tribal | Council Member | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Tribal | Emergency Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Tribal | Emergency Operations Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Tribal | Treasurer | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Madera County Tribal | Tribal Chairperson | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Tribal | Tribal Secretary | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Madera County Tribal | Vice Chairperson | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Madera County Water and Waste Water Facility | County of Madera | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Mariposa County | Battalion Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Cal FIRE Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Command Center | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Mariposa County | Councilmember | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | County Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | County Clerk | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | County Health officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | County Supervisor | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Mariposa County | Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Division Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Emergency Command Center | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Emergency Dispatch | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Emergency Services | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Mariposa County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | GIS Specialist | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | MHOAC | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | OES Coordinator | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Public Information officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Sergeant Special Operations | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County | Unit Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Mariposa County Communication Facility | AT&T Services Inc | Tier 2 | 10/15/2024 07:13 PDT
Mariposa County Communication Facility | Sierra Telephone Company Inc | Tier 3 | 10/15/2024 07:05 PDT
Mariposa County Emergency Services Facility | USDI-NPS-Yosemite | Tier 2 | 10/15/2024 07:05 PDT
Mendocino County | Acting Emergency Services Coordinator | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Board Chair | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Board Vice Chair | Tier 3 | 10/15/2024 07:21 PDT
Mendocino County | County Clerk/Assessor/Recorder | Tier 3 | 10/15/2024 07:21 PDT
Mendocino County | County Supervisor | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | County supervisor | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Fire Chief | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Interim County Executive officer | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Lieutenant | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Local Cal Fire | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | MHOAC | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | OES Coordinator | Tier 3 | 10/15/2024 07:21 PDT
Mendocino County | Sheriff | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County | Supervisor | Tier 3 | 10/15/2024 07:22 PDT
Mendocino County CCA | General | Tier 3 | 10/15/2024 07:22 PDT
Merced County | Battalion Chief | HFRA | 10/15/2024 07:22 PDT
Merced County | Board Vice Chair | HFRA | 10/15/2024 07:22 PDT
Merced County | Cal FIRE Chief | HFRA | 10/15/2024 07:22 PDT
Merced County | County Clerk | HFRA | 10/15/2024 07:21 PDT
Merced County | County Executirve officer | HFRA | 10/15/2024 07:22 PDT
Merced County | District 4 Supervisor | HFRA | 10/15/2024 07:23 PDT
Merced County | Duty Chief | HFRA | 10/15/2024 07:22 PDT
Merced County | Fire Chief | HFRA | 10/15/2024 07:22 PDT
Merced County | General | HFRA | 10/15/2024 07:22 PDT
Merced County | OES Coordinator | HFRA | 10/15/2024 07:21 PDT
Merced County | OES Director | HFRA | 10/15/2024 07:22 PDT
Merced County | Sheriff | HFRA | 10/15/2024 07:22 PDT
Merced County | Supervisor | HFRA | 10/15/2024 07:22 PDT
Merced County | Supervisor District 1 | HFRA | 10/15/2024 07:22 PDT
Merced County | Unit Chief | HFRA | 10/15/2024 07:22 PDT
Merced County Gustine | City Manager | HFRA | 10/15/2024 07:22 PDT
Merced County Gustine | Emergency | HFRA | 10/15/2024 07:22 PDT
Monterey County | Board Chair | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Board Member | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | County Supervisor - District 2 | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Duty officer | Tier 2 | 10/15/2024 07:23 PDT
Monterey County | Emergency Services Manager | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Emergency Services Planner | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Fire Chief | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | General | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Medical Health Operational Area Coordinator | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | MHOAC | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | OES Director | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | On Call contact | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Sheriff | Tier 2 | 10/15/2024 07:21 PDT
Monterey County | Sr. Emergency Services Coordination | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | Supervisor | Tier 2 | 10/15/2024 07:22 PDT
Monterey County | UNIT CHIEF | Tier 2 | 10/15/2024 07:22 PDT
Monterey County CCA | General | Tier 2 | 10/15/2024 07:22 PDT
Monterey County Communication Facility | American Tower Corporation | Tier 2 | 10/15/2024 07:05 PDT
Monterey County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:05 PDT
Monterey County Communication Facility | AT&T Services Inc | Tier 2 | 10/15/2024 07:05 PDT
Monterey County Communication Facility | Dept of The Army | Tier 2 | 10/15/2024 07:04 PDT
Monterey County Communication Facility | Verizon | Tier 2 | 10/15/2024 07:04 PDT
Monterey County Emergency Services Facility | California Department of Forestry | Tier 2 | 10/15/2024 07:05 PDT
Monterey County Other Facility | Department of The Army | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 19:43 PDT
Monterey County Other Facility | Dept of The Army | Tier 2 | 10/15/2024 07:04 PDT
Monterey County Water and Waste Water Facility | Dept of The Army | Tier 2 | 10/15/2024 07:04 PDT
Napa County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | County Clerk/Recorder | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | Emergency Services officer | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Napa County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | GIS | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Napa County | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | Interim County Executive officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | Medical Health Operational Area Coordinator | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | MHOAC | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Napa County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Napa County | Under-Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County CCA | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Napa County Communication Facility | AT&T Mobility LLC | Tier 3, Tier 2 | 10/15/2024 07:05 PDT
Napa County Communication Facility | AT&T Services Inc | Tier 3 | 10/15/2024 07:13 PDT
Napa County Communication Facility | California Highway Patrol | Tier 2 | 10/15/2024 07:13 PDT
Napa County Communication Facility | Comcast | Tier 3 | 10/16/2024 08:07 PDT
Napa County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 10/16/2024 08:07 PDT
Napa County Communication Facility | T-Mobile West Corporation | Tier 3 | 10/15/2024 07:05 PDT
Napa County Emergency Services Facility | California Department of Forestry | Tier 3 | 10/16/2024 08:07 PDT
Napa County Emergency Services Facility | County of Napa | Tier 3 | 10/15/2024 07:05 PDT
Napa County Emergency Services Facility | Napa County Department of Public Works | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/16/2024 08:08 PDT
Napa County Saint Helena | City Manager | Tier 3 | 10/15/2024 07:22 PDT
Napa County Saint Helena | Fire Chief | Tier 3 | 10/15/2024 07:22 PDT
Napa County Water and Waste Water Facility | California Department of Forestry | Tier 3 | 10/16/2024 08:07 PDT
Nevada County | Assistant Director | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Board Chair | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Board Vice Chair | Tier 1, Tier 2 | 10/15/2024 07:21 PDT
Nevada County | Chief | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | County Executive officer | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Director | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Division Chief | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Fire Chief | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | General | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Health officer | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Local Cal Fire | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Sheriff | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County | Supervisor | Tier 1, Tier 2 | 10/15/2024 07:22 PDT
Nevada County Communication Facility | AT&T Services Inc | Tier 2 | 10/15/2024 07:04 PDT
Nevada County Communication Facility | AT&T Wireless Service LLC | Tier 2 | 10/15/2024 07:13 PDT
Nevada County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 10/15/2024 07:05 PDT
Nevada County Communication Facility | Qwest Communications International Inc | Tier 2 | 10/15/2024 07:05 PDT
Nevada County Communication Facility | T-Mobile West LLC | Tier 2 | 10/15/2024 07:05 PDT
Nevada County Communication Facility | USA Media Group | Tier 2 | 10/15/2024 07:05 PDT
Nevada County Communication Facility | Verizon | Tier 2 | 10/15/2024 19:43 PDT
Nevada County Communication Facility | Verizon Services Corporation | Tier 2 | 10/15/2024 07:05 PDT
Nevada County Energy Sector Facility | Sierra Pacific Power Co | Tier 2 | 10/15/2024 07:05 PDT
Placer County | Assistant Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Assistant Director | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Board Chair | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Board Vice Chair | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Building Maintenance Superintendent | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | CEO | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | CIO | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Captain - PCSO | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | County Clerk/Recorder | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | County Executirve officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Deputy Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Deputy Director | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Deputy Director of Communications and Public Affairs | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Director | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Duty officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Placer County | Emergency Command Center | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Emergency Services Coordinator | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Facilities, Emergency | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | General | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Health officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | IT Manager | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Placer County | IT Supervisor | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Lieutenant - PCSO | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Local Cal Fire | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Main Telecom Number | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Placer County Supervisor, District Two | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Public Health officer | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Placer County | Roads Manager | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Sergeant - PCSO | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Sheriff Dispatch | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County | Supervisor | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Placer County CCA | General | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Placer County Communication Facility | AAT Communications Corporation | Tier 2 | 10/15/2024 07:05 PDT
Placer County Communication Facility | AT&T Mobility LLC | Tier 3 | 10/15/2024 07:13 PDT
Placer County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Placer County Communication Facility | T-Mobile West LLC | Tier 2 | 10/15/2024 07:05 PDT
Placer County Communication Facility | USA Media Group | Tier 2 | 10/15/2024 07:05 PDT
Placer County Communication Facility | Verizon | Tier 3 | 10/15/2024 07:05 PDT
Placer County Emergency Services Facility | Truckee Fire Protection Dist | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 19:43 PDT
Placer County Other Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Plumas County | CAO | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | County Administrative officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | County Clerk-Recorder-Registrar | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | Director | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Plumas County | Director of Nursing | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | Program Division Chief- Emergency Preparedness office | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Plumas County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:05 PDT
Plumas County Communication Facility | Sprint Corporation | Tier 3 | 10/15/2024 07:13 PDT
Plumas County Energy Sector Facility | City of Santa Clara | Tier 3 | 10/15/2024 07:04 PDT
San Benito County | County Administrative officer | HFRA, Tier 2 | 10/16/2024 08:00 PDT
San Benito County | Emergency Manager | HFRA, Tier 2 | 10/16/2024 07:59 PDT
San Benito County | Emergency Services Specialist | HFRA, Tier 2 | 10/16/2024 07:59 PDT
San Benito County | Non-Emergency | HFRA, Tier 2 | 10/16/2024 08:00 PDT
San Benito County | Sheriff | HFRA, Tier 2 | 10/16/2024 08:00 PDT
San Benito County | Staff Analyst | HFRA, Tier 2 | 10/16/2024 07:59 PDT
San Benito County | Supervisor | HFRA, Tier 2 | 10/16/2024 07:59 PDT
San Benito County CCA | General | HFRA, Tier 2 | 10/16/2024 07:59 PDT
San Benito County Communication Facility | Pinnacles Tel Co | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/16/2024 08:07 PDT
San Luis Obispo County | Duty Chief | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
San Luis Obispo County | Duty officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
San Luis Obispo County | Emergency Services Manager | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
San Luis Obispo County | Fire Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
San Luis Obispo County | General | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
San Luis Obispo County | OES Duty officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
San Luis Obispo County | Watch Commander | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
San Luis Obispo County CCA | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
San Luis Obispo County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:05 PDT
San Luis Obispo County Communication Facility | AT&T Services Inc | Tier 3 | 10/15/2024 07:04 PDT
San Luis Obispo County Emergency Services Facility | California Highway Patrol | Tier 2 | 10/15/2024 07:13 PDT
Santa Barbara County | Fire Chief | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Santa Barbara County | OEM Duty officer | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Santa Barbara County | OES Director | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Santa Barbara County | Sheriff | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Santa Barbara County CCA | General | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Santa Barbara County Communication Facility | American Tower Corporation | Tier 2 | 10/15/2024 07:05 PDT
Santa Barbara County Communication Facility | California Highway Patrol | Tier 2 | 10/15/2024 07:05 PDT
Santa Barbara County Communication Facility | Frontier Communications Corporation Dip | Tier 3 | 10/15/2024 07:04 PDT
Santa Barbara County Communication Facility | SBA Towers Vi, LLC | Tier 3 | 10/16/2024 08:08 PDT
Santa Clara County | Assistant Chief / Assistant Director / MHOAC | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Board President | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County | Board Vice Chair | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County | Chief Operating officer | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | County Executive officer | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | County Supervisor | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Deputy CEO | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Deputy Director | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Director | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Director of Emergency Management | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Duty officer | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Emergency | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Emergency Preparedness Manager | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Fire Chief | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | General | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County | Main Line | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Non-Emergency | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Policy Director - office of Supervisor Simitian | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Public Health officer | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Sheriff | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County | Supervisor | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County | Train Ops | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County | Watch Commander | HFRA, Tier 2, Tier 3 | 10/16/2024 08:00 PDT
Santa Clara County CCA | General | HFRA, Tier 2, Tier 3 | 10/16/2024 07:59 PDT
Santa Clara County Communication Facility | American Tower Corporation | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Communication Facility | AT&T Mobility LLC | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/16/2024 08:07 PDT
Santa Clara County Communication Facility | Comcast of California | Tier 2 | 10/16/2024 09:46 PDT
Santa Clara County Communication Facility | Crown Castle International | Tier 2 | 10/16/2024 08:07 PDT
Santa Clara County Communication Facility | Frontier Communications Corporation Dip | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Communication Facility | Verizon | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Milpitas | City Clerk | Tier 2 | 10/16/2024 17:55 PDT
Santa Clara County Milpitas | City Manager | Tier 2 | 10/16/2024 08:00 PDT
Santa Clara County Milpitas | Council Member | Tier 2 | 10/16/2024 17:55 PDT
Santa Clara County Milpitas | Deputy City Manager | Tier 2 | 10/16/2024 08:00 PDT
Santa Clara County Milpitas | Emergency | Tier 2 | 10/16/2024 07:59 PDT
Santa Clara County Milpitas | Fire Chief | Tier 2 | 10/16/2024 07:59 PDT
Santa Clara County Milpitas | Mayor | Tier 2 | 10/16/2024 17:55 PDT
Santa Clara County Milpitas | Non-Emergency | Tier 2 | 10/16/2024 08:00 PDT
Santa Clara County Milpitas | Police Chief | Tier 2 | 10/16/2024 17:55 PDT
Santa Clara County Milpitas | Public Works Director | Tier 2 | 10/16/2024 07:59 PDT
Santa Clara County Milpitas | Vice Mayor | Tier 2 | 10/16/2024 17:55 PDT
Santa Clara County Other Facility | California Department of Forestry | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Other Facility | D B Leeson & B S Leeson | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County Other Facility | US National Weather Service | Tier 3 | 10/16/2024 09:46 PDT
Santa Clara County San Jose | Acting Director | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Assistant City Manager | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Assistant Director | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | City Clerk | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County San Jose | Chief of Staff | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | City Manager | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County San Jose | Communications officer | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Council Member | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Deputy City Manager | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Deputy Director | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Director Clean Energy | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County San Jose | Director PRNS | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Director, office of Emergency Management | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Fire Chief | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Clara County San Jose | Mayor | HFRA, Tier 2, Tier 3 | 10/16/2024 17:55 PDT
Santa Clara County San Jose | Senior Advisor | HFRA, Tier 2, Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | ADEC | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Assistant CAO | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Board Chair | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Board Vice Chair | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Communications Director | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | County Administrative officer | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Emergency Coordinator | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Fire Chief | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | MHOAC | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Main office | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Non-Emergency | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | OES Duty officer | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Sheriff | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Supervisor | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County | Undersheriff | Tier 3 | 10/16/2024 09:57 PDT
Santa Cruz County CCA | General | Tier 3 | 10/16/2024 09:57 PDT
Shasta County | Fire Chief | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | General | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Interim Tribal Administrator | HFRA, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Shasta County | Lieutenant | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | office of Emergency Services Coordinator | HFRA, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Shasta County | Operations Manager | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Regional Disaster Medical Health Coordinator and Specialist | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Sergeant | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Sheriff-Coroner | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Staff Chief, Northern Operations | HFRA, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Shasta County | Tribal Chairman | HFRA, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Shasta County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:05 PDT
Shasta County Communication Facility | Cingular Wireless Services, Inc | Tier 2 | 10/16/2024 08:07 PDT
Shasta County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 10/15/2024 07:04 PDT
Shasta County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 10/15/2024 07:05 PDT
Shasta County Communication Facility | Happy Valley Telephone Co | Tier 2 | 10/15/2024 07:05 PDT
Shasta County Communication Facility | US Department of Agriculture | Tier 2 | 10/16/2024 08:07 PDT
Shasta County Communication Facility | Verizon | Tier 2 | 10/15/2024 07:13 PDT
Shasta County Emergency Services Facility | California Department of Forestry | Tier 2 | 10/15/2024 07:05 PDT
Shasta County Emergency Services Facility | County of Shasta | Tier 2 | 10/15/2024 07:05 PDT
Shasta County Emergency Services Facility | French Gulch Volunteer Fire | Tier 2 | 10/15/2024 07:13 PDT
Shasta County Major Transportation Facility | California Highway Patrol | Tier 2 | 10/15/2024 07:05 PDT
Shasta County Water and Waste Water Facility | US Bureau Of Reclamation | Tier 3 | 10/15/2024 07:05 PDT
Sierra County | Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Chair, Supervisor District 4 | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Coordinator | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | County Clerk/Recorder | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Dispatch Supervisor | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Sierra County | Fire Chief | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Sheriff-Coroner / OES Director | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Superintendent | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Supervisor | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County | Vice Chair | HFRA, Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sierra County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 10/15/2024 07:04 PDT
Sierra County Communication Facility | California Highway Patrol | Tier 3 | 10/15/2024 19:43 PDT
Sierra County Communication Facility | US Department of Agriculture | Tier 3 | 10/15/2024 19:43 PDT
Sierra County Emergency Services Facility | Downieville Fire District | Tier 3 | 10/15/2024 19:43 PDT
Sierra County Emergency Services Facility | Sierra City Fire Protection District | Tier 2 | 10/15/2024 07:13 PDT
Sierra County Energy Sector Facility | Henwood Associate Inc | Tier 2 | 10/15/2024 07:05 PDT
Sierra County Government - Jail Facility | County of Sierra | Tier 3 | 10/15/2024 07:05 PDT
Sierra County Other Facility | Crown Castle Usa Inc | Tier 3 | 10/15/2024 19:43 PDT
Sierra County Other Facility | Sierra City Fire Dept Auxiliary | Tier 2 | 10/15/2024 07:13 PDT
SIERRA County Water and Waste Water Facility | Downieville Public Utilities District | Tier 3 | 10/15/2024 07:05 PDT
SIERRA County Water and Waste Water Facility | Haskell Creek Tract Association | Tier 1 | 10/15/2024 07:05 PDT
Solano County | Board Chair | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | County Administrator | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | County Clerk | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | Dispatch | HFRA, Tier 2 | 10/15/2024 07:23 PDT
Solano County | Emergency | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | Fire Chief | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | MHOAC - EMS Administrator | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | Sheriff | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County | Supervisor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County CCA | General | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Communication Facility | American Tower Corp | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | American Tower Corporation | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:04 PDT
Solano County Communication Facility | AT&T Services Inc | Tier 2 | 10/15/2024 07:04 PDT
Solano County Communication Facility | AT&T Wireless Service LLC | HFRA | 10/15/2024 07:05 PDT
Solano County Communication Facility | Comcast Cable Communications Management LLC | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | Comcast Fresno LLC | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | Crown Castle International | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | T-Mobile West Corporation | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | TCI | Tier 2 | 10/15/2024 07:05 PDT
Solano County Communication Facility | Verizon | Tier 2 | 10/15/2024 07:04 PDT
Solano County Emergency Services Facility | Vacaville Fire Protection District | Tier 2 | 10/15/2024 07:13 PDT
Solano County Fairfield | City Clerk | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | City Manager | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | Council Member | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | Councilmember | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | Emergency | Tier 2 | 10/15/2024 07:23 PDT
Solano County Fairfield | Fire Chief | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | General | Tier 2 | 10/15/2024 07:23 PDT
Solano County Fairfield | Mayor | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | Police Chief | Tier 2 | 10/15/2024 07:22 PDT
Solano County Fairfield | Vice Mayor | Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | Assistant City Manager | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | Chief of Police | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | City Clerk | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | City Manager | HFRA, Tier 2 | 10/15/2024 07:21 PDT
Solano County Vacaville | Council Member | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | Emergency | HFRA, Tier 2 | 10/15/2024 07:23 PDT
Solano County Vacaville | General | HFRA, Tier 2 | 10/15/2024 07:23 PDT
Solano County Vacaville | Mayor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Solano County Vacaville | Utilities Operations and Maintenance Manager | HFRA, Tier 2 | 10/15/2024 07:23 PDT
Solano County Vacaville | Vice Mayor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Sonoma County | 1st District Sonoma County Supervisor | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Sonoma County | Board Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Board Chair Pro Tem | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Board Vice Chair | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Community Alert & Warning Manager | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Sonoma County | Deputy Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Director | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Division Chief | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | EMS | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | EMS Dispatch | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Fire Captain | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | MHOAC | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Main office | Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Sonoma County | Sheriff | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Sheriff Dispatch | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Sheriff's Liaison | Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Sonoma County | Staff Duty officer | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County | Supervisor | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County CCA | General | Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Communication Facility | AT&T Mobility LLC | Tier 3 | 10/15/2024 07:05 PDT
Sonoma County Communication Facility | AT&T Services Inc | Tier 3 | 10/15/2024 07:04 PDT
Sonoma County Communication Facility | California Highway Patrol | Tier 2 | 10/17/2024 04:12 PDT
Sonoma County Communication Facility | Comcast Fresno LLC | Tier 3 | 10/15/2024 07:05 PDT
Sonoma County Communication Facility | Frontier Communications Corporation Dip | Tier 3 | 10/15/2024 07:04 PDT
Sonoma County Communication Facility | T Mobile West A Delaware Corp | Tier 3 | 10/15/2024 07:05 PDT
Sonoma County Communication Facility | T-Mobile USA | Tier 3 | 10/16/2024 08:07 PDT
Sonoma County Communication Facility | T-Mobile West LLC | Tier 3 | 10/16/2024 08:07 PDT
Sonoma County Communication Facility | Verizon | Tier 3 | 10/16/2024 08:07 PDT
Sonoma County Emergency Services Facility | Sonoma Valley Fire District | Tier 3 | 10/15/2024 07:05 PDT
Sonoma County Santa Rosa | Chief of Police | Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Santa Rosa | City Council Member | Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Santa Rosa | Council Member | Tier 3 | 10/15/2024 07:21 PDT
Sonoma County Santa Rosa | Deputy Emergency Manager | Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Santa Rosa | Division Chief Fire Marshal | Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Santa Rosa | Mayor | Tier 3 | 10/15/2024 07:21 PDT
Sonoma County Santa Rosa | Police Chief | Tier 3 | 10/15/2024 07:22 PDT
Sonoma County Santa Rosa | Vice Mayor | Tier 3 | 10/15/2024 07:22 PDT
Stanislaus County | Board Chair | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Chief Executive officer | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | County Clerk Recorder | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | EMS Duty officer | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Emergency Manager | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Fire Chief | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Health officer | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | MHOAC | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Public Health Duty officer | HFRA | 10/15/2024 07:23 PDT
Stanislaus County | Sheriff | HFRA | 10/15/2024 07:22 PDT
Stanislaus County | Supervisor | HFRA | 10/15/2024 07:22 PDT
Stanislaus County Communication Facility | Federal Bureau of Investigation | HFRA | 10/15/2024 07:05 PDT
Tehama County | Chief Administrator | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Tehama County | Communications Supervisor | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Tehama County | County Clerk / Recorder | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Tehama County | Lieutenant and OES manager | HFRA, Tier 2 | 10/15/2024 07:21 PDT
Tehama County | OES Director | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Tehama County | Sheriff | HFRA, Tier 2 | 10/15/2024 07:22 PDT
Tehama County Communication Facility | AT&T Mobility | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Communication Facility | AT&T Services Inc | Tier 2 | 10/15/2024 07:04 PDT
Tehama County Communication Facility | Charter Communications Holding Company LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Tehama County Communication Facility | Ducor Telephone Co | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Communication Facility | Ducor Telephone Corp | Tier 2 | 10/15/2024 07:04 PDT
Tehama County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Communication Facility | T Mobile West A Delaware Corp | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Communication Facility | T-Mobile West LLC | Tier 2 | 10/15/2024 07:13 PDT
Tehama County Communication Facility | Verizon | Tier 2 | 10/15/2024 07:04 PDT
Tehama County Corning | City Clerk | Tier 2 | 10/15/2024 07:22 PDT
Tehama County Corning | City Manager | Tier 2 | 10/15/2024 07:22 PDT
Tehama County Corning | Police Chief | Tier 2 | 10/15/2024 07:22 PDT
Tehama County Emergency Services Facility | California Department of Forestry | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Emergency Services Facility | County of Tehama | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:05 PDT
Tehama County Government - Jail Facility | California Department of Corrections | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Other Facility | Burns, Sherri | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Other Facility | California Department of Forestry | Tier 2 | 10/15/2024 07:05 PDT
Tehama County Red Bluff | Chief of Police | Tier 2 | 10/15/2024 07:22 PDT
Tehama County Red Bluff | City Manager | Tier 2 | 10/15/2024 07:22 PDT
Tuolumne County | County Administrator | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | County Clerk | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Emergency Command Center | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | General | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Tuolumne County | Local Cal Fire | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:23 PDT
Tuolumne County | MHOAC | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | OES | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Office of Emergency Services Assistant Director | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Public Health Director | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Sheriff | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Supervisor | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Tuolumne County | Supervisor, District 4 | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Tuolumne County Board of Supervisors - District 1 | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:22 PDT
Tuolumne County | Unit Chief | Tier 1, Tier 2, Tier 3 | 10/15/2024 07:21 PDT
Tuolumne County Communication Facility | American Tower Corporation | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Communication Facility | AT&T Services Inc | Tier 3 | 10/15/2024 07:04 PDT
Tuolumne County Communication Facility | Comcast Cable Communications Management, LLC | Tier 3 | 10/15/2024 07:04 PDT
Tuolumne County Communication Facility | Comcast Fresno LLC | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Communication Facility | New Cingular Wireless PCS, LLC | Tier 3 | 10/15/2024 07:13 PDT
Tuolumne County Communication Facility | Sierra Nevada Communications | Tier 3 | 10/15/2024 07:04 PDT
Tuolumne County Communication Facility | T-Mobile West LLC | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Communication Facility | Tuolumne Cablevision | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Communication Facility | Verizon Wireless | Tier 3 | 10/15/2024 19:43 PDT
Tuolumne County Emergency Services Facility | County of Tuolumne | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Water and Waste Water Facility | Leland Meadows Water | Tier 3 | 10/15/2024 19:43 PDT
Tuolumne County Water and Waste Water Facility | Slide Inn Water Co LLC | Tier 3 | 10/15/2024 07:05 PDT
Tuolumne County Water and Waste Water Facility | Tuolumne Utilities District | Tier 3 | 10/15/2024 07:05 PDT
Yolo County | Board Chair | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Board Vice Chair | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | County Administrator | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | County Clerk-Recorder | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | County OES Supervisor | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Deputy County Administrator | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Dispatch | Tier 2 | 10/15/2024 07:23 PDT
Yolo County | EMS Administrator | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Fire Chief | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Non-Emergency | Tier 2 | 10/15/2024 07:23 PDT
Yolo County | Sheriff | Tier 2 | 10/15/2024 07:22 PDT
Yolo County | Supervisor | Tier 2 | 10/15/2024 07:21 PDT
Yolo County CCA | General | Tier 2 | 10/15/2024 07:22 PDT
Yolo County Communication Facility | AT&T Mobility LLC | Tier 2 | 10/15/2024 07:05 PDT
Yolo County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote) | 10/15/2024 07:13 PDT
Yolo County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 10/15/2024 07:05 PDT

## Table F-1
Table F-1. Community Resource Centers Provided by PG&E
# | County | Site Name | Address | Operating Hours (PDT) |  |  |  | Total Visitors | Indoor / Outdoor | Amenities Provided
|  |  |  | Day 1 10-17 | Day 2 10-18 | Day 3 10-19 | Day 4 10-20
1 | Butte | Forest Ranch Baptist Church | 4967 Schott Road | No | 12:00 – 22:00 | 08:00 – 1830 | No | 21 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
2 | Butte | Magalia Pines Baptist Church | 14098 Skyway Rd | No | 12:00 – 22:00 | 08:00 – 15:30 | No | 5 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
3 | Butte | Concow Elementary School | 11679 Nelson Bar Rd | No | 12:00 – 22:00 | 08:00 – 20:00 | No | 9 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
4 | Colusa | Stonyford Community Hall | 229 Market St | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 2200 | 08:00– 10:30 | 223 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
5 | Contra Costa | Clayton Community Church | 6055 Main Street | 18:00 – 22:00 | 08:00 – 22:00 | 08:00 – 19:00 | No | 73 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
6 | Contra Costa | Balfour-Guthrie Park | 1701 Balfour Rd | 18:00 – 22:00 | 08:00 – 22:00 | 0800 – 19:00 | No | 80 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
7 | Fresno | Auberry Library | 33049 Auberry Rd | No | 08:00 – 22:00 | 08:00 – 11:00 | No | 11 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
8 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309 | 08:00 – 22:00 | 08:00 – 22:00 | 0800 – 22:00 | 08:00 – 09:00 | 225 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
9 | Lake | Live Oaks Senior Center | 12502 Foothill Blvd | 1200 – 2200 | 08:00 – 22:00 | 08:00 – 19:00 | No | 540 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
10 | Lake | Hidden Valley Lake Association | 19305 Donkey Hill Rd | 1200 – 2200 | 08:00 – 22:00 | 08:00 – 19:00 | No | 722 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
11 | Madera | North Fork Elementary School | 33087 Rd 228 | No | 08:00 – 22:00 | 08:00 – 11:30 | No | 10 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
12 | Madera | Oakhurst Community Hall | 39800 Fresno Flats Rd | No | 08:00 – 22:00 | 08:00 – 11:30 | No | 29 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
13 | Monterey | San Antonio Union School | 67550 Lockwood Jolon Road | No | 08:00 – 22:00 | 08:00 – 14:30 | No | 199 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
14 | Monterey | Salinas Valley Fairgrounds | 625 Division St. | No | 08:00 – 22:00 | 08:00 – 14:30 | No | 32 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
15 | Napa | Pacific Union College | 200 Angwin Ave | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 14:00 | 186 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
16 | Napa | Calistoga Community Center | 1307 Washington Street | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 14:00 | 56 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
17 | Santa Barbara | Santa Maria Elks Lodge | 1309 N Bradley Rd | No | 08:00 – 22:00 | 08:00 – 12:30 | No | 17 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
18 | Santa Clara | Mayfair Community Center | 2039 Kammerer Ave | No | 12:00 – 22:00 | 08:00 – 18:00 | No | 141 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
19 | Santa Clara | Morgan Hill Library | 660 W Main Ave | No | 12:00 – 22:00 | 08:00 – 15:00 | No | 38 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
20 | Santa Clara | Faith Lutheran Church | 16548 Ferris Ave | No | 12:00 – 22:00 | 08:00 – 17:00 | No | 12 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
21 | Santa Cruz | Unitarian Universalist Fellowship | 6401 Freedom Blvd | No | 12:00 – 22:00 | 08:00 – 16:00 | No | 21 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
22 | Shasta | Risen King Community Church | 6100 Oasis Rd | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 14:30 | No | 62 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
23 | Shasta | Happy Valley Community Center | 5400 Happy Valley Rd | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 14:30 | No | 56 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
24 | Solano | Solano Community College | 2001 N Village Pkwy | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 21:30 | No | 59 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
25 | Solano | Green Valley Golf Course | 35 Country Club Road | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 21:30 | No | 194 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
26 | Sonoma | First Congregational Church of Sonoma | 252 W Spain St | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 16:30 | No | 96 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
27 | Sonoma | Healdsburg Community Church | 1100 University Street | 12:00 – 22:00 | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 11:00 | 155 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
28 | Tehama | Rancho Tehama Association | 17605 Park Terrace Road | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 17:30 | No | 756 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.
29 | Tehama | Flournoy Elementary School | 15850 Paskenta Rd | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 17:30 | No | 158 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating.