## Table 1
Table 1: Customers Notified and De-energized1
Total Customers |  |  | MBL Customers | Counties | Tribes | Circuits |  |  | Damage Count | CFI De-energized
Notified | De-energized | Canceled | De-energized | De-energized | De-energized | Transmission De-energized | Unique Distribution Circuits in Any Version of Scope | Distribution Circuits De-energized
14,098 2 | 9,176 3 | 4779 | 853 | 5 | 2 | 5 | 43 | 20 | 1 | 176
1 The information, times, and figures referenced in this report are based on the best available information available at the time of the report’s submission. The information, times, and figures herein are subject to revision based on further analysis and validation.
2 Of the 14,098 customers notified of planned PSPS impact, 169 customers received a notice that they may be de-energized but did not receive a cancellation and are not counted as a de-energized customer. See Section 5.5 and 5.7 for more information.
3 Of the 9,176 customers de-energized, 34 customers did not receive any notifications before de-energization. 33 of these customers were among the 52 reported in Section 5.5 that had no valid contact information. See Section 5.5 for more information.

## Table 2
Table 2: 2024 PSPS Risk-Benefit Consequence Modelling Considerations
Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outage events.1
Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
Table 3: Notification Descriptions
Type of Notification | Recipients | Description
PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs,1 transmission level customers, and municipal utilities | On September 27, 2024, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E is monitoring an increased potential of PSPS outages. Following PG&E’s activation of its EOC, the following was completed: •PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS. •PG&E sent notifications to other Public Safety Partners2 via call, text, and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When weather is anticipated to pass.
o Estimated Time of Restoration (ETOR).
o Links to the PSPS Portal where event-specific maps and information are available.
• Local PG&E representatives called potentially impacted County OES and select Tribes to inform them that PG&E is monitoring an increased potential of PSPS.
WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES. • PG&E sent notifications to other Public Safety Partners, transmission level customers, municipal utilities, and all customers via call, text message and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When the adverse weather is anticipated to pass.
o ETOR.
o For Public Safety Partners only: Links to the PSPS Portal.
o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support, and the Portable Battery Program.
o For transmission-level customers only: Transmission Substation Name and Line name serving substation.
•PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification.
•PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL Program customers, SIV Program customers), transmission level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications to other Public Safety Partners, transmission-level customers, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.” • PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would be shut off. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission level customers3, and municipal utilities | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES representatives that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers. • PG&E sent notifications to other Public Safety Partners, municipal utilities, transmission level customers and customers via call, text messages, and e-mail, which included:
o Impacted addresses (for customers only).
o De-energization time.
o When the adverse weather is anticipated to pass.
o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the Portable Battery Program.
Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission level customers, and municipal utilities | After the weather event had passed and the area is deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission level customers4, municipal utilities and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include:
o New field or meteorology conditions.
o Damage was found during patrols and repair is needed.
Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission level customers, and municipal utilities | GCC conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including MBL Program customers and SIV customers, were restored, they received notifications via call, text and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text and e-mail. Public Safety Partner notifications were provided in English.
1 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
2 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.
3 Transmission-level customers receive a GCC live call before de-energization and prior to re-energization.
4 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 4
Table 4: Customer Notification Timeline Summary
Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Distributed by:
Pre-De-energization (Prior) | 72-48 hours | Tribal/Local Governments and CCAs* | 2024-09-28 03:37 | Priority |  | PG&E
|  | Public Safety Partners** | 2024-09-28 03:41 | Priority |  | PG&E
|  | Public Safety Partners** | 2024-09-28 04:37 | Priority |  | PG&E
| 48-24 hours | Tribal/Local Governments and CCAs* | 2024-09-28 14:35 | Watch |  | PG&E
|  | Tribal/Local Governments and CCAs* | 2024-09-29 03:21 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-09-28 14:13 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-09-29 03:27 | Watch |  | PG&E
|  | All Customers*** | 2024-09-28 15:20 | Watch |  | PG&E
|  | All Customers*** | 2024-09-29 03:26 | Watch |  | PG&E
| 24-12 hours2 | Tribal/Local Governments and CCAs* | 9/29/2024 10:40 | Watch |  | PG&E
|  | Public Safety Partners** | 2024-09-29 10:45 | Watch |  | PG&E
|  | All Customers*** | 2024-09-29 10:44 | Watch |  | PG&E
| 4-1 hours | Tribal/Local Governments and CCAs* | 9/30/2024 1:44 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 9/30/2024 2:39 | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 9/30/2024 16:03 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-09-30 01:50 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-09-30 02:43 | Warning |  | PG&E
|  | Public Safety Partners** | 2024-09-30 16:14 | Warning |  | PG&E
|  | All Customers*** | 2024-09-30 01:47 | Warning |  | PG&E
|  | All Customers*** | 2024-09-30 02:42 | Warning |  | PG&E
|  | All Customers*** | 2024-09-30 16:07 | Warning |  | PG&E
Initiation (During) | When De-energization is initiated | Public Safety Partners** | 2024-09-30 02:15 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 04:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 05:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 05:30 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 05:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 06:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 06:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 06:32 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 06:45 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 08:01 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 08:16 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 08:30 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 08:47 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 09:32 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 09:46 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 13:12 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 13:13 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 13:15 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-09-30 13:19 | Power Off |  | PG&E
|  | Public Safety Partners** | 2024-10-01 08:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 02:15 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 04:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 05:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 05:30 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 05:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 06:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 06:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 06:32 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 06:45 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 08:01 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 08:16 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 08:30 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 08:47 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 09:32 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 09:46 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 13:12 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 13:13 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 13:15 | Power Off |  | PG&E
|  | All Customers*** | 2024-09-30 13:19 | Power Off |  | PG&E
|  | All Customers*** | 2024-10-01 08:46 | Power Off |  | PG&E
Initiation (During) | Immediately before re-energization | Tribal/Local Governments and CCAs* | 9/30/2024 16:22 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | Tribal/Local Governments and CCAs* | 9/30/2024 16:29 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-09-30 02:18 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-09-30 13:48 | Inspecting/ Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 2024-09-30 14:02 | Inspecting/ Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 2024-09-30 14:19 | Inspecting/ Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 2024-10-01 11:48 | Inspecting/ Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 2024-10-01 13:18 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | All Customers*** | 2024-09-30 02:18 | Inspecting/ Weather All-Clear | First All-Clear Notification sent. | PG&E
|  | All Customers*** | 2024-09-30 13:48 | Inspecting/ Weather All-Clear |  | PG&E
|  | All Customers*** | 2024-09-30 14:02 | Inspecting/ Weather All-Clear |  | PG&E
|  | All Customers*** | 2024-09-30 14:19 | Inspecting/ Weather All-Clear |  | PG&E
|  | All Customers*** | 2024-10-01 11:48 | Inspecting/ Weather All-Clear |  | PG&E
|  | All Customers*** | 2024-10-01 13:18 | Inspecting/ Weather All-Clear | Last All-Clear Notification sent. | PG&E
|  | Public Safety Partners** | 2024-09-30 13:16 | ETOR Update | First ETOR Update Notification sent. | PG&E
|  | Public Safety Partners** | 2024-09-30 14:20 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 15:34 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 15:50 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 16:04 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 16:20 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 16:35 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 17:05 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 17:19 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 17:34 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 17:50 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 18:04 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 18:20 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 19:04 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 19:49 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 20:19 | ETOR Update |  | PG&E
|  | Public Safety Partners** | 2024-09-30 20:50 | ETOR Update | Last ETOR Update Notification sent. | PG&E
|  | All Customers*** | 2024-09-30 13:16 | ETOR Update | First ETOR Update Notification sent. | PG&E
|  | All Customers*** | 2024-09-30 14:20 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 15:34 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 15:50 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 16:04 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 16:20 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 16:35 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 17:05 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 17:19 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 17:34 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 17:50 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 18:04 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 18:20 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 19:04 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 19:49 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 20:19 | ETOR Update |  | PG&E
|  | All Customers*** | 2024-09-30 20:50 | ETOR Update | Last ETOR Update Notification sent. | PG&E
Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 10/1/2024 13:29 | Restore |  | PG&E
|  | Public Safety Partners** | 2024-09-30 03:17 | Restore | First initial Restoration Notification sent. | PG&E
|  | Public Safety Partners** | 2024-10-01 13:32 | Restore | Last initial Restoration Notification sent. | PG&E
|  | All Customers*** | 2024-09-30 03:17 | Restore | First Restoration Notification sent. | PG&E
|  | All Customers*** | 2024-10-01 13:32 | Restore | Last Restoration Notification sent. | PG&E
Cancelation | Within 2 hours of decision to cancel | Tribal/Local Governments and CCAs* | 9/29/2024 9:42 | Cancel | Only Tribal/Local Government s and CCAs removed from scope received cancel notification. The decision to descope these customers was made 9/29/2024 9:05 AM
|  | Tribal/Local Governments and CCAs* | 9/30/2024 14:27 | Cancel
|  | Tribal/Local Governments and CCAs* | 10/1/2024 9:31 | Cancel
|  | Public Safety Partners** | 2024-09-29 09:52 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 9/29/2024 9:05 AM.
|  | Public Safety Partners** | 2024-09-30 14:29 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 9/30/2024 13:45.
|  | Public Safety Partners** | 2024-10-01 09:32 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 10/1/2024 8:36.
|  | All Customers*** | 2024-09-29 09:52 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 9/29/2024 9:05 .
|  | All Customers*** | 9/30/2024 14:29 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 9/30/2024 13:45.
|  | All Customers*** | 2024-10-01 09:32 | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made 10/1/2024 8:36.
Ad Hoc Notification | N/A | Customers at risk of a second de-energization window | 2024-09-30 17:29 | Ad Hoc | Only customers at risk of a second de-energization received this ad hoc notification. | PG&E
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators.
**A subset of Public Safety Partners, including water, wastewater, and communication service providers.
***All Customers, including MBL Program customers and SIV Program customers.
1 D.19-05-042, Appendix A, Timing of Notification.
2 While not a CPUC requirement, PG&E provides an additional 24-12 hour notification to Tribal/Local Governments, Public Safety Partners and Customers.

## Table 5
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted1
Designation | Total Number of customers2 | Notification Attempts Made3 | Timing of Attempts4 (PDT) | Who made the Notification Attempt | Successful Positive Notification5
MBL6 | 1173 | 1,169 Watch Notifications | 2024-09-28 14:14 | PG&E | 1,126 Watch Notifications
|  | 1,042 Warning Notifications | 2024-09-29 20:42 |  | 899 Warning Notifications
|  | 2,211 Overall Notifications | 2024-09-28 14:14 |  | 2,025 Overall Notifications
MBL behind a master meter7 | 17 | 17 Watch Notifications | 2024-09-28 14:22 | PG&E | 3 Watch Notifications
|  | 17 Warning Notifications | 2024-09-30 01:49 |  | 2 Warning Notifications
|  | 34 Overall Notifications | 2024-09-28 14:22 |  | 5 Overall Notifications
SIV | 454 | 449 Watch Notifications | 2024-09-28 14:14 | PG&E | 423 Watch Notifications
|  | 410 Warning Notifications | 2024-09-29 08:44 |  | 336 Warning Notifications
|  | 859 Overall Notifications | 2024-09-28 14:14 |  | 759 Overall Notifications
1 Counts of Notification Attempts Made will not reflect the actual total of customers notified as both MBL and SIV Program customers can appear in both subset groups.
2 Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
3 Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
4 Initial start time notification was sent.
5 PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
6 Residential tenants of master-metered customers can also qualify for Medical Baseline quantities. The Medical Baseline category for the purposes of Table 5 does not include MBL Program customers who are master meter tenants.
7 PG&E has additional processes in place to ensure MBL customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.
[1] Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
[2] Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
[3] Initial start time notification was sent.
[4] PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.

## Table 6
Table 6: Outcomes of Notifications to De-energized Medical Baseline Program Customers
Count | Type of Notifications to De-energized MBL Customers1 | Description
853 | Total De-energized MBL Program Customers | The number of customers de-energized who participate in PG&E’s MBL Program.
853 | Total Notifications Attempted/Sent | The total sum of automated notifications attempted via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls.
0 | Total Notifications Not Attempted/Sent | Total MBL Program customers de-energized that PG&E did not attempt to notify.
847 | Total Notifications Delivered | The total sum of automated notifications sent via call, text, and e-mail.
6 | Total Notifications Not Delivered2 | Total MBL Program customers de-energized whose notification was not delivered.
723 | Total Notifications Initially Acknowledged | The total sum of automated notifications sent via call, text and email where notification was acknowledged.
736 | Total In-Person Visits/Doorbell Rings and Live Agent Phone Calls | Total attempted doorbell ring for impacted MBL Program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.3 This includes call attempts made by Live Agent representatives to MBL Program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit. Refer to Table 7 for the detailed breakdown of this category.
828 | Total Notifications Received | Customers who acknowledged their notification by taking one of the following actions: answered an automated or Live Agent phone call, responded to a text message, opened an e-mail, or greeted an in-person doorbell ring (excludes voicemails left, text message delivered only and not confirmed, door hanger left).
25 | Total Notifications Not Received | Total MBL Program customers who did not confirm receipt/acknowledge their automated notifications, Live Agent phone calls or in-person doorbell ring. Customers who did not answer a doorbell ring were left a door hanger.
1 Based on SPID.
2 Customers received Doorbell Rings.
3Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 7
Table 7: Count and Type of Additional Notifications to De-energized Medical Baseline Program Customers
Count | Type of Additional Notifications to Impacted Medical Baseline Customers1 | Description
186 | Total In-Person Visits/Doorbell Rings | Doorbell ring attempts to impacted MBL Program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.2
550 | Live Agent Phone Calls | Calls made by Live Agent representatives to MBL Program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit.
1 Based on SPID.
2 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 8
Table 8: Notification Failure Causes
Notifications Sent to: | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
Public Safety Partners excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 0 | No failures.
| Entities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Entities who did not receive any notifications before de-energization | 0 | No failures.
| Entities who were not notified immediately before re-energization | 0 | No failures.
| Entities who did not receive cancellation notification within two hours of the decision to cancel | 1 | A manual error in creating data files resulted in a missed cancellations to one agency. PG&E will clarify process documentation and ensure that those responsible for preparing the notification files are aware of how scope changes affect incorporated and unincorporated territories.
CFI2 | Facilities who did not receive 48-to 72-hour priority notification | 0 | No failures.
| Facilities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Facilities who did not receive any notifications before de-energization | 0 | No failures.
| Facilities who were not notified at de-energization initiation | 16 | See Table 8A and 8B.
| Facilities who were not notified immediately before re-energization | 8 | See Table 8A and 8C.
| Facilities who were not notified when re-energization is complete | 1 | See Table 8A.
| Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
All other affected customers | Customers who did not receive 24–48-hour advance notifications | 1 | This customer’s transformer was recently installed and was not properly reflected in PG&E’s datasets used to determine planned PSPS impacts. As a result, this customer was not identified as a planned impact for this PSPS, and thus did not receive any PSPS notifications prior to de-energization.
| Customers who did not receive 1–4-hour imminent notifications | 1
| Customers who did not receive any notifications before de-energization | 1
| Customers who were not notified at de-energization initiation | 479 (includes 47 MBL) | See Table 8A and 8B.
| Customers who were not notified immediately before re-energization | 454 (includes 45 MBL) | See Table 8A and 8C.
| Customers who were not notified when re-energization is complete | 11 | See Table 8A.
| Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
1 Only includes Tribes, cities, counties, and CCAs.
2 Includes Public Safety Partners who are critical facilities and infrastructure customers.

## Table 8A
Table 8A: Explanation of Failures for Critical Facility and Infrastructure and All Other Affected Customers Who Were Not Notified at De-energization Initiation, Immediately Before Re-energization, and When Re-energization was Complete
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
0 | 2 | These customers were assigned to the wrong transformer in the data system used for in-outage and post-outage notifications. The transformer they were incorrectly assigned to was experiencing an extended outage. As a result, these customers were not identified as impacted customers for the PSPS outages, and thus did not receive notifications at de-energization initiation, immediately before re-energization and when re-energization was complete. However, these customers did receive pre-outage PSPS notifications. A field check will be performed to identify the correct transformer assignment for these customers.
0 | 3 | These customers did not receive notifications at de-energization initiation, immediately before re-energization and when re-energization was complete. This occurred because these customers were not included in the table of customer contact information used to launch automated notifications through our internal outage platform. As a result, they could not be notified. The root cause of their exclusion from this table is under investigation.
1 | 0 | This facility did not receive notifications at de-energization initiation, immediately before re-energization and when re-energization was complete due to incorrect categorization. The categorization indicated this facility was not in service on our internal data platform used for in-outage and post-outage notifications. A mapping correction was processed to fix the error and has been completed prior to submission of this report. These customers did receive pre-outage PSPS notifications.
0 | 2 | These customers did not receive notifications at de-energization initiation, immediately before re-energization and when re-energization was complete. Recent structure damage was modeled incorrectly in the system used for in-outage and post-outage notifications. As a result, these customers were inadvertently categorized as experiencing an extended outage, and thus did not receive the notifications that would be sent to customers impacted by a PSPS outage. These customers did receive pre-outage PSPS notifications. A field check will be performed to resolve the error.
0 | 4 | These customers did not receive notifications at de-energization initiation, immediately before re-energization and when re-energization was complete due to being impacted by an extended outage. The extended outage was restored prior to the start of the PSPS, but our data systems for in-outage and post-outage notifications were not updated to reflect this restoration. As a result, these customers did not receive the notifications that would be sent to customers impacted by a PSPS outage. These customers did receive pre-outage PSPS notifications.

## Table 8B
Table 8B: Explanation of Failures for Critical Facility and Infrastructure and All Other Affected Customers Who Received Delayed Notifications at De-Energization Initiation
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
15 | 468 (includes 47 MBL) | These customers received a delayed notification for de-energization initiation due to a vendor error. The notification vendor, Message Broadcast, experienced a network disruption causing notification launch delays. As a result, these notifications were sent between three to four and a half hours after the time of de-energization initiation.

## Table 8C
Table 8C: Explanation of Failures for Critical Facility and Infrastructure and All Other Affected Customers Who Were Not Notified Immediately Before Re-energization
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
0 | 2 | These customers were not notified immediately before re-energization due to a categorization error in our internal outage platform.
7 | 441 (includes 45 MBL) | These customers were not notified immediately before re-energization due to a systems issue. Our internal outage management tool is automatically checked for updates at regular intervals for the purpose of generating PSPS in-outage and post-outage notifications. The notification immediately before re-energization for these customers was triggered during a one-second gap between these automatic checks, which meant this notification was not caught by these checks and thus was not generated.

## Table 9
Table 9: Explanation of False Positive Communications
Impact | Count of Critical Facilities | Count of All Other Affected Customers | Explanation
Customers notified that PSPS de-energization would occur but did not experience an outage. | 0 | 1 (no MBL) | This customer was linked to the wrong transformer in the data systems used for PSPS scoping, pre-outage, in-outage, and post-outage notifications. The transformer incorrectly linked to this customer was planned for and ultimately de-energized, but the actual transformer feeding this customer was not impacted by this PSPS. As a result, this customer received pre-, in-, and post-outage PSPS notifications without actually experiencing de-energization.
| 0 | 5 (no MBL) | The transformer serving these customers was on an extended outage prior to and during this PSPS due to fire damage, and should have been excluded from the planned PSPS impacts. However, these customers were incorrectly entered in our customer data system, which caused these customers to be included within the planned PSPS scope. As a result, these customers received pre-outage PSPS notifications indicating they would be de-energized. The transformer serving these customers was on an extended outage prior to and during this PSPS due to fire damage, and should have been excluded from the planned PSPS impacts. However, these customers were incorrectly entered in our customer data system, which caused these customers to be included within the planned PSPS scope. As a result, these customers received pre-outage PSPS notifications indicating they would be de-energized. These customers did not receive in-outage and post-outage PSPS notifications.
| 0 | 3 (no MBL) | The transformer serving these customers was experiencing an extended outage prior to the PSPS for non-fire related reasons and these customers were being energized by generator. These customers were not removed from the planned scope of PSPS impacts. As a result, they received pre-outage notifications indicating they would be impacted by the PSPS. These customers did not receive in-outage and post-outage PSPS notifications.
Critical facilities and other affected customers de-energized for a non-PSPS outage but were incorrectly notified that their outage was due to PSPS. | 8 | 341 (includes 2 MBL) | Prior to de-energization, an unplanned EPSS outage occurred on a circuit that was not planned for PSPS impact. Due to a manual error, PSPS impacts were inadvertently assigned to the EPSS outage. As a result, these customers received PSPS-specific in-outage notifications rather than non-PSPS notifications associated with their outage. This error was discovered and addressed prior to restoration.

## Table 10
Table 10: PSPS Portal Time & Date for Map Sharing
Date | Time PDF and GIS Maps Shared (PDT)
2024-09-28 | 2:42
2024-09-28 | 13:19
2024-09-29 | 9:18
2024-09-30 | 1:43
2024-09-30 | 14:02
2024-10-01 | 8:57

## Table 11
Table 11: PSPS Notifications Submitted to Cal OES
Date | Time PDF and GIS Maps Shared (PDT)
2024-09-28 | 2:12
2024-09-28 | 7:05
2024-09-28 | 14:54
2024-09-29 | 6:08
2024-09-29 | 9:24
2024-09-29 | 14:47
2024-09-29 | 22:46
2024-09-30 | 4:49
2024-09-30 | 6:05
2024-09-30 | 8:04
2024-09-30 | 14:03
2024-10-01 | 13:01

## Table 12
Table 12: PSPS Notifications Submitted to Cal CPUC
Date | Time PDF and GIS Maps Shared (PDT)
2024-09-28 | 2:27
2024-09-29 | 9:57
2024-09-29 | 23:59
2024-09-30 | 4:24
2024-09-30 | 5:44
2024-09-30 | 9:22
2024-09-30 | 14:27
2024-09-30 | 16:40
2024-10-01 | 8:50
2024-10-01 | 13:27

## Table 13
Table 13: Customer Notifications Based on Language Preference
Language | Total Notifications1 | Percent
English | 630149 | 99.34%
Spanish | 3700 | 0.58%
Chinese (Mandarin & Cantonese) | 447 | 0.07%
Russian | 27 | 0.004%
Vietnamese | 16 | 0.003%
Total | 634339 | 100%
1 Total notifications do not include doorbell rings and Live Agent phone calls.

## Table 14
Table 14: Call Center Support Services1
Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls (seconds) | Number of Calls Handled by Call Center Translation Services | Number of Languages Supported by Call Center Translation Services
42899 | 529 | 8 | 813 | 240
55 Metrics are provided from September 28, 2024, through October 1, 2024.

## Table 15
Table 15: Generators Available for Critical Facilities and Infrastructure Customers
Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
Diesel Generator | 2 | 0.065 | 31 | 2 units on reserve in San Leandro.
Diesel Generator | 5 | 0.1 | 25.3 | 5 units on reserve in Sacramento.
Diesel Generator | 1 | 0.125 | 25 | 1 unit on reserve in San Leandro.
Diesel Generator | 6 | 0.2 | 22.9 | 6 units on reserve in San Leandro.
Diesel Generator | 1 | 0.275 | 26 | 1 unit on reserve in Sacramento.
Diesel Generator | 2 | 0.57 | 24 | 2 units on reserve at San Leandro.
Diesel Generator | 7 | 1.5 | 10 | 7 units on reserve in Martinez.
Diesel Generator | 8 | 1 | 35 | 3 units pre-staged at ICU Hospitals and 5 units on reserve at Sacramento.
Diesel Generator | 8 | 1.14 | 24 | 8 on reserve in San Leandro
Diesel Generator | 17 | 2 | 27.7 | 17 units on reserve total, 7 in Sacramento and 10 at San Leandro.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 16
Table 16: Critical Facility and Infrastructure Customers Energized with Backup Generation
County | Site Type | Generation Deployed | Duration of Operation (PDT) | Reason Deployed
Shasta | CAL FIRE Happy Valley Fire Center | .1 MW | 25:15 hours | Public Safety

## Table 17
Table 17: Number and Nature of Complaints due to the September 30 – October 1, 2024 PSPS
Nature of Complaints | Number of Complaints
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 16
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 18
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 1
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 35
Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 1

## Table 18
Table 18: Count and Type of Claim(s) Received
Description of Claims | Number of Claims
Business Interruption/Economic Loss | 1
Food Loss Only | 1
Property Damage | 1

## Table 19
Table 19: Weather All-Clear Times
All-Clear Zones | Weather All-Clear Date and Time (PDT)
241C, 244A, 244B, 247A | 2024-09-30 12:13
170B, 177A, 241A, 245A, 245B, 245C, 246A, 246C, 246F, 246G, 246H, 246I 248A, 249, 280C, 280G, 280H, 285A | 2024-09-30 13:30

## Table 20
Table 20: Temporary Substation Generation
County | Site Type | Generation Deployed | Duration of Operation | Reason Deployed
Glenn | Elk Creek Substation | 6 MW | 51:20 hours | Customer Mitigation

## Table 21
Table 21: Lessons Learned from the PSPS
Issue | Discussion | Resolution
Customer Notification | Customers were incorrectly mapped, which resulted in missed notifications.1 | We corrected the customer’s mapping to prevent future missed notifications and continue to refine our process.
Customer Notification | Customers were de-energized for a non-PSPS outage unrelated to this PSPS but were incorrectly notified that their outage was due to a PSPS.2 | We corrected the outage classification in the system as soon as the issue was identified. We plan to review processes with personnel responsible and consider additional training.
Customer Notifications | The notification vendor experienced a service interruption, which caused a delay in launching some notifications.3 | We are coordinating with the vendor to implement a monitoring system that will provide alerts when this type of issue arises as well as working to improve the resilience of the data preparation process.
Public Safety Partner Notifications | A manual error occurred when creating data files that resulted in a missed cancellation notification to one jurisdiction.4 | We plan to clarify process documentation and ensure that those responsible for preparing notification files are aware of how scope changes affect incorporated and unincorporated territories.
1 See Table 8A and Table 9 for more information.
2 See Table 9 for more information.
3 See Table 8B for more information.
4 See Table 8 for more information.

## Table 22
Table 22: Maximum Wind Gusts Recorded September 30 – October 1, 2024 in Impacted Counties
County | Maximum Wind Gust (mph) | Station ID | Station Name
Butte | 46 mph | JBGC1 | Jarbo Gap
Colusa | 26 mph | PG598 | Rail Canyon Road
Glenn | 36 mph | PG845 | Road 65
Shasta | 43 mph | PC073 | Slate Creek
Tehama | 37 mph | PG855 | Black Butte Lake

## Table A-1.1
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the September 30 – October 1, 2024 PSPS
Circuit Name | Time Place | Forecast | [18 empty] | Agency |  |  |  | Observed
|  | ws_ mph | ws_ mph_ 50m | wg_ ec_ mph | temp_2m_f | flame_ length_ ft_2hr | rate_ of_ spread_chhr_2hr | area_ acres_ 8hr | rh_ 2m | vpd2m_mb | prob_cat | dfm_ 10hr | dfm_ 100 hr | dfm_ 1000 hr | lfm_ herb | lfm_ woody | lfm_ chamise_new | sum_ tree ovr | prob_ ignition | cfpd | HWW | HWA | RFW | GACC_High Risk | ws_ mph | wg_ mph | temp_f | RH_% | ws_ mph_ AC | wg_ mph_ AC | temp_f_AC | RH_%_AC | open_ psps_ tags | Tx impacts_yes_no | PSPS Potential Risk Consequence | PSPS Potential Benefit
ANTLER 1101 | TP2 | 19 | 33 | 45 | 90 | 25.1 | 31.3 | 1547.9 | 10.9 | 43.1 | 0.936 | 0.038 | 0.064 | 0.085 | 38 | 74 | 68 | 49813.6 | 0.0024101 | 14.5 | No | No | No | No | 13 | 27 | 95 | 15 | 10 | 18 | 87 | 15 | Yes | No | 0.1 | 20.9
BIG BEND 1101 | TP17 | 21 | 34 | 49 | 92 | 13.2 | 69.1 | 4650 | 9.6 | 46 | 0.979 | 0.035 | 0.06 | 0.079 | 32 | 70 | 67 | 54176.2 | 0.0042988 | 30.1 | No | No | No | Yes | 31 | 46 | 96 | 12 | 24 | 44 | 88 | 13 | Yes | No | 0.3 | 530.7
CEDAR CREEK 1101 | TP1 | 33 | 44 | 64 | 91 | 41 | 48 | 2916.6 | 10.2 | 44.2 | 0.951 | 0.038 | 0.062 | 0.083 | 37 | 76 | 69 | 87136.2 | 0.0070787 | 33.2 | No | No | No | No | 20 | 41 | 97 | 11 | 9 | 16 | 77 | 19 | Yes | No | 0.2 | 70.1
CLARK ROAD 1102 | TP17 | 29 | 37 | 48 | 96 | 17.2 | 86.5 | 7077.5 | 8.7 | 52.3 | 0.981 | 0.033 | 0.059 | 0.077 | 31 | 76 | 65 | 21285.1 | 0.003877 | 30.1 | No | No | No | Yes | 31 | 46 | 96 | 12 | 23 | 44 | 89 | 13 | Yes | No | 0.2 | 1105.8
COTTONWOOD 1102 | TP3 | 18 | 26 | 39 | 96 | 10 | 85.8 | 9423.4 | 9 | 52.2 | 0.913 | 0.035 | 0.062 | 0.076 | 31 | 58 | 62 | 5633.5 | 0.0011352 | 6.9 | No | No | No | Yes | 18 | 31 | 91 | 12 | 20 | 29 | 91 | 12 | Yes | No | 1 | 200.4
CRESTA 1101 | TP17 | 19 | 30 | 45 | 90 | 7.5 | 35.3 | 2722.7 | 10.3 | 43.8 | 0.954 | 0.037 | 0.063 | 0.082 | 41 | 77 | 69 | 3924.9 | 0.0013381 | 9.1 | No | No | No | No | 22 | 30 | 83 | 12 | 24 | 44 | 79 | 16 | Yes | No | 0.3 | 371.4
ELK CREEK 1101 | TP5 | 23 | 33 | 44 | 97 | 14.5 | 117.7 | 39036 | 8.2 | 54.6 | 0.97 | 0.031 | 0.057 | 0.067 | 30 | 58 | 57 | 3559.7 | 0.0011858 | 9.3 | No | No | No | Yes | 21 | 28 | 94 | 11 | 14 | 22 | 94 | 11 | Yes | No | 0.6 | 602.4
GIRVAN 1101 | TP3 | 21 | 31 | 47 | 96 | 13.3 | 87.5 | 17299 | 8.9 | 53.2 | 0.967 | 0.034 | 0.06 | 0.071 | 30 | 65 | 61 | 23867.7 | 0.0033553 | 24.3 | No | No | No | Yes | 23 | 40 | 92 | 10 | 20 | 29 | 92 | 10 | Yes | No | 0.2 | 358.8
GIRVAN 1102 | TP3 | 20 | 29 | 42 | 96 | 11.7 | 54.9 | 4427 | 9.1 | 51.6 | 0.947 | 0.035 | 0.062 | 0.083 | 36 | 69 | 65 | 20596.5 | 0.0024649 | 15.4 | No | No | No | Yes | 18 | 35 | 92 | 11 | 20 | 29 | 92 | 11 | Yes | No | 0.1 | 1294.8
GLENN 1101 | TP5 | 24 | 32 | 43 | 98 | 11.9 | 151.5 | 50957 | 8.2 | 56.7 | 0.958 | 0.032 | 0.058 | 0.068 | 30 | 67 | 58 | 14.6 | 0.0021486 | 10.9 | No | No | No | Yes | 26 | 37 | 91 | 10 | 19 | 27 | 92 | 9 | Yes | No | 0.1 | 4.3
JESSUP 1101 | TP3 | 18 | 28 | 43 | 96 | 13.3 | 57.8 | 4745 | 8.9 | 53.2 | 0.961 | 0.035 | 0.062 | 0.073 | 32 | 67 | 64 | 16150.9 | 0.0020012 | 13.5 | No | No | No | Yes | 23 | 40 | 91 | 10 | 20 | 29 | 92 | 10 | Yes | No | 0.1 | 10.5
JESSUP 1102 | TP3 | 20 | 30 | 42 | 96 | 9.6 | 66.5 | 5895 | 9 | 52.2 | 0.94 | 0.035 | 0.063 | 0.081 | 35 | 75 | 64 | 16150.9 | 0.0020594 | 14.1 | No | No | No | Yes | 18 | 31 | 90 | 11 | 20 | 29 | 92 | 11 | Yes | No | 0.1 | 10.6
KESWICK 1101 | TP3 | 20 | 33 | 48 | 95 | 16.6 | 74.7 | 6044.1 | 9.6 | 49.9 | 0.976 | 0.035 | 0.062 | 0.077 | 38 | 68 | 67 | 2943 | 0.0023145 | 17.4 | No | No | No | Yes | 18 | 35 | 97 | 6 | 13 | 23 | 97 | 6 | Yes | No | 1.1 | 376.9
LOGAN CREEK 2102 | TP5 | 26 | 32 | 43 | 99 | 12.1 | 155.1 | 63238 | 8.1 | 57.9 | 0.919 | 0.031 | 0.059 | 0.074 | 30 | 63 | 58 | 547 | 0.0016714 | 10.8 | No | No | No | Yes | 27 | 36 | 92 | 12 | 18 | 25 | 93 | 12 | Yes | No | 0.2 | 19.9
OREGON TRAIL 1102 | TP2 | 21 | 31 | 45 | 96 | 13.4 | 55.2 | 3414.8 | 8.4 | 52.9 | 0.964 | 0.033 | 0.058 | 0.08 | 35 | 67 | 66 | 26609.3 | 0.0034862 | 18.7 | No | No | No | Yes | 15 | 30 | 97 | 11 | 13 | 23 | 97 | 11 | Yes | No | 0.1 | 21.3
PIT NO 3 2101 | TP1 | 22 | 34 | 51 | 89 | 43.6 | 33.4 | 1046.3 | 11.6 | 40.6 | 0.863 | 0.042 | 0.067 | 0.093 | 50 | 83 | 69 | 57069.9 | 0.0036951 | 19.1 | No | No | No | No | 9 | 23 | 94 | 1 | 5 | 12 | 65 | 1 | Yes | No | 1.6 | 1262.5
ROUND MOUNTAIN 1101 | TP1 | 27 | 35 | 43 | 87 | 37.2 | 37.3 | 1971.5 | 11.4 | 38.6 | 0.765 | 0.041 | 0.067 | 0.086 | 43 | 81 | 70 | 9575.7 | 0.0018407 | 7.1 | No | No | No | No | 20 | 41 | 89 | 14 | 9 | 16 | 72 | 19 | Yes | No | 0.5 | 1661.6
STILLWATER 1101 | TP2 | 22 | 31 | 48 | 95 | 12.7 | 48.9 | 1792.2 | 9.4 | 50.4 | 0.947 | 0.035 | 0.062 | 0.079 | 35 | 73 | 66 | 36401.9 | 0.0034862 | 19.9 | No | No | No | Yes | 26 | 38 | 97 | 11 | 19 | 29 | 97 | 11 | Yes | No | 0.3 | 140.1
STILLWATER 1102 | TP2 | 22 | 33 | 46 | 96 | 8 | 52.3 | 4457.6 | 8.9 | 52.2 | 0.963 | 0.035 | 0.06 | 0.078 | 34 | 68 | 66 | 26610.9 | 0.0034862 | 25.4 | No | No | No | Yes | 26 | 38 | 97 | 11 | 19 | 29 | 97 | 11 | Yes | No | 1.8 | 1217.7
WHITMORE 1101 | TP1 | 21 | 33 | 49 | 88 | 12.3 | 29.5 | 1427.7 | 10.9 | 40.5 | 0.904 | 0.037 | 0.062 | 0.085 | 42 | 80 | 68 | 68805.8 | 0.0040004 | 21.2 | No | No | No | Yes | 10 | 26 | 95 | 12 | 3 | 7 | 83 | 20 | Yes | No | 1.6 | 2004.4

## Table A-1.2
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the September 30 – October 1, 2024 PSPS
Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all- clear time.
Observed | Observed temp_f | Observed Temperature during Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
Observed | open_psps_tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based)
Observed | Tx_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de- energization of upstream transmission lines, regardless of whether those distribution lines would have also been de- energized due to direct distribution PSPS.
Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
Forecast | wg_ec_mph | Forecasted Peak Wind Gust | mph | max | Wind gust in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technosylva.
Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technosylva.
Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
Forecast | sum_tree_ovr | Tree Overstrike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
Forecast | prob_ignition | Ignition Probability Weather (IPW) Model Output | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis
Forecast | cfpd | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution. Scaled by 1000 to convert to an integer value.

## Table A-2.1
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the September 30 – October 1, 2024 PSPS
Forecast | [9 empty] | Agency |  |  |  | Forecast | [9 empty] | Observed | [10 empty] | PSPS Risk vs. Benefit
Circuit Name | ws_mph | ws_mph_50m | wg_ec_mph | temp_2m_f | flame_length_ft_2hr | rate_of_spread_chhr_2hr | area_acres_8hr | rh_2m | vpd2m_mb | HWW | HWA | RFW | GACC_High Risk | prob_cat | dfm_10hr | dfm_100hr | dfm_1000hr | lfm_herb | lfm_woody | lfm_chamise_new | sum_tree_ovr | OA | CFPt | Observed ws_mph | Observed wg_mph | Observed temp_f | Observed RH_% | Observed ws_mph_AC | Observed wg_mph_AC | Observed temp_f_AC | Observed RH_%_AC | High Fire Risk Area (Y/N) | High Risk Vegetation Present on Circuit (Y/N) | Tx_impacts_yes_no | PSPS Potential Risk Consequence | PSPS Potential Benefit
CASCADE-BENTON-DESCHUTES | 20 | No | 34 | 88 | 7 | 40 | 1596 | 11 | 40 | No | No | No | No | 0.556 | 0.048 | 0.069 | No | 36 | No | 66 | No | 0.0116 | 3.45 | 23 | 40 | 97 | 9 | 15 | 27 | 100 | 9 | Yes | No | No | 0.1 | 790.9
ELK CREEK TAP | 25 | No | 43 | 92 | 12 | 138 | 53230 | 9 | 47 | No | No | No | No | 0.348 | 0.041 | 0.07 | No | 30 | No | 60 | No | 0.014 | 1.62 | 23 | 31 | 93 | 11 | 16 | 22 | 94 | 11 | Yes | No | No | 0.1 | 66.8
KILARC-CEDAR CREEK | 26 | No | 44 | 81 | 13 | 30 | 1703 | 14 | 32 | No | No | No | No | 0.687 | 0.049 | 0.071 | No | 42 | No | 69 | No | 0.00365 | *1 | 20 | 41 | 85 | 17 | 15 | 29 | 86 | 16 | Yes | No | No | 0.1 | 94.8
PIT #4 TAP | 22 | No | 37 | 72 | 16 | 21 | 1047 | 18 | 22 | No | No | No | No | 0.507 | 0.056 | 0.074 | No | 49 | No | 70 | 10.1 | 4.78e-11 | 0 | 9 | 23 | 79 | 15 | 7 | 18 | 81 | 16 | Yes | Yes | No | 0.1 | 9.8
PIT #6 TAP | 19 | No | 37 | 66 | 10 | 17 | 903 | 21 | 18 | No | No | No | No | 0.402 | 0.063 | 0.078 | No | 49 | No | 70 | 7.2 | 1.23e-06 | 0 | 5 | 13 | 74 | 19 | 4 | 13 | 76 | 18 | Yes | Yes | No | 0.1 | 9.6
1This information is not available at the time of submission and is currently under review. We will provide an update in the 2024 PSPS Post-Season Report.

## Table A-2.2
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the September 30 – October 1, 2024 PSPS
Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
Forecast | wg_ec_mph | Gust wind speeds | mph | max | Wind gust in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface
Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100. PG&E does not utilize this factor in the decision to shutoff power.
Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water). PG&E does not utilize this factor in the decision to shutoff power.
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
Forecast | sum_tree_ovr | Tree Overstike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft. PG&E does not utilize this factor in the decision to shutoff power.
Forecast | cfpt_vegsum | Catastrophic Fire Potential Vegetation | ft | mas | A risk-based assessment of the probability of tree fall-ins combined with the probability of catastrophic fires. Not included in Table A-2.1 per CPUC template, however, PG&E utilizes it as a decision making factor.
Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis
Forecast | CFPt | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
Forecast | ustar_frc_vel | Shear Velocity | mps | max | Wind shear stress in velocity terms. Not included in Table A-2.1 per CPUC template, however, PG&E utilizes it as a decision making factor.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed wg_mph | Observed Wind gust during Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed temp_f | Observed Temperature during event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed wg_mph_AC | Observed Sustained Wind gust at All Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear- | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
Observed | High Fire Risk Area | High Fire Risk Area | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through High Fire Risk Area.
Observed | High Risk Vegetation Present on Circuit | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit. PG&E does not utilize this factor in the decision to shutoff power.
Observed | Transmission_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Table B-1
Table B-1. Circuits De-Energized During the September 30 – October 1, 2024 PSPS
Distribution / Transmission | Circuit Name | De-Energization Date and Time | All-Clear Date and Time | Restoration Date and Time | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | MBL Customers | AFN other than MBL Customers | Other Customers
Distribution | ANTLER 1101 | 2024-09-30 08:18 | 2024-09-30 12:13 | 2024-09-30 14:32 | SHASTA | Tier 2 | 65 | 63 | 2 | 6 | 17 | 0
Distribution | BIG BEND 1101 | 2024-09-30 04:40 | 2024-09-30 13:30 | 2024-09-30 19:04 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 196 | 173 | 21 | 15 | 58 | 2
Distribution | CEDAR CREEK 1101 | 2024-09-30 05:44 | 2024-09-30 12:13 | 2024-10-01 10:36 | SHASTA | Tier 3, Tier 2 | 684 | 618 | 61 | 58 | 203 | 5
Distribution | CLARK ROAD 1102 | 2024-09-30 04:44 | 2024-09-30 13:30 | 2024-09-30 18:25 | BUTTE | Tier 3, Tier 2 | 212 | 193 | 16 | 18 | 64 | 3
Distribution | COTTONWOOD 1102 | 2024-09-30 09:30 | 2024-09-30 13:30 | 2024-09-30 16:23 | SHASTA | Tier 2 | 58 | 51 | 4 | 5 | 19 | 3
Distribution | CRESTA 1101 | 2024-09-30 04:38 | 2024-09-30 13:30 | 2024-09-30 18:26 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 6 | 1 | 3 | 0 | 0 | 2
Distribution | ELK CREEK 1101 | 2024-09-30 07:56 | 2024-09-30 13:30 | 2024-09-30 19:16 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 658 | 547 | 89 | 39 | 143 | 22
Distribution | GIRVAN 1101 | 2024-09-30 09:27 | 2024-09-30 13:30 | 2024-09-30 18:18 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 1215 | 1104 | 105 | 122 | 220 | 6
Distribution | GIRVAN 1102 | 2024-09-30 09:24 | 2024-09-30 13:30 | 2024-09-30 16:41 | SHASTA | Tier 3 | 339 | 332 | 7 | 28 | 75 | 0
Distribution | GLENN 1101 | 2024-09-30 07:59 | 2024-09-30 13:30 | 2024-09-30 17:43 | GLENN, TEHAMA | Partially Outside HFTD, Tier 2 | 149 | 83 | 43 | 4 | 18 | 23
Distribution | JESSUP 1101 | 2024-09-30 09:27 | 2024-09-30 13:30 | 2024-09-30 16:33 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 1355 | 1321 | 32 | 156 | 446 | 2
Distribution | JESSUP 1102 | 2024-09-30 09:33 | 2024-09-30 13:30 | 2024-09-30 18:26 | SHASTA | Partially Outside HFTD, Tier 2 | 1190 | 1152 | 35 | 108 | 407 | 3
Distribution | KESWICK 1101 | 2024-09-30 10:01 | 2024-09-30 13:30 | 2024-10-01 00:01 | SHASTA | Tier 3 | 22 | 4 | 17 | 0 | 1 | 1
Distribution | LOGAN CREEK 2102 | 2024-09-30 07:57 | 2024-09-30 13:30 | 2024-09-30 16:40 | GLENN | Partially Outside HFTD, Tier 2 | 59 | 27 | 13 | 0 | 0 | 19
Distribution | OREGON TRAIL 1102 | 2024-09-30 08:21 | 2024-09-30 13:30 | 2024-09-30 18:14 | SHASTA | Partially Outside HFTD, Tier 2 | 810 | 759 | 51 | 84 | 222 | 0
Distribution | PIT NO 3 2101 | 2024-09-30 05:44 | 2024-09-30 13:30 | 2024-10-01 10:01 | SHASTA | Partially Outside HFTD, Tier 2 | 24 | 19 | 5 | 0 | 0 | 0
Distribution | ROUND MOUNTAIN 1101 | 2024-09-30 05:51 | 2024-09-30 12:13 | 2024-09-30 13:53 | SHASTA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
Distribution | STILLWATER 1101 | 2024-09-30 08:17 | 2024-09-30 13:30 | 2024-09-30 19:07 | SHASTA | Partially Outside HFTD, Tier 2 | 659 | 576 | 77 | 71 | 210 | 6
Distribution | STILLWATER 1102 | 2024-09-30 08:18 | 2024-09-30 13:30 | 2024-09-30 17:30 | SHASTA | Partially Outside HFTD, Tier 2 | 13649 | 13289 | 36 | 126 | 360 | 0
Distribution | WHITMORE 1101 | 2024-09-30 05:45 | 2024-09-30 12:13 | 2024-09-30 17:50 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 110 | 101 | 8 | 13 | 36 | 1
Transmission | CASCADE-BENTON-DESCHUTES | 2024-09-30 09:08 | 2024-09-30 13:30 | 2024-09-30 15:38 | SHASTA | Partially Outside HFTD, HFTD Tier 2, HFTD Tier 1 | 0 | 0 | 0 | 0 | 0 | 0
Transmission | ELK CREEK TAP | 2024-09-30 08:30 | 2024-09-30 13:30 | 2024-09-30 17:48 | GLENN | Partially Outside HFTD, HFTD Tier 2, HFTD Tier 1 | 1 | 0 | 0 | 0 | 0 | 0
Transmission | KILARC-CEDAR CREEK | 2024-09-30 06:14 | 2024-09-30 12:13 | 2024-09-30 15:40 | SHASTA | HFTD Tier 3 | 0 | 0 | 0 | 0 | 0 | 0
Transmission | PIT #4 TAP | 2024-09-30 06:48 | 2024-09-30 12:13 | 2024-09-30 17:02 | SHASTA | HFTD Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
Transmission | PIT #6 TAP | 2024-09-30 06:45 | 2024-09-30 12:13 | 2024-09-30 16:43 | SHASTA | HFTD Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
Total | [6 empty] | 917682 | 84524 | 625 | 853 | 2499 | 98

## Table C-1
Table C-1. Damages & Hazards Found Within the De-Energized Areas
Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage/ Hazard | Type of Damage/Hazard | Description of Damage
Cedar Creek 1101 | Shasta | 101547319 | Tier 2 | Damage | Wind related | Broken tie wire

## Table D-1
Table D-1. Public Safety Partners Contacted
Organization/Jurisdiction | Title | HFTD or HFRA Tier1 | Date/Time Contacted (PDT)
Alameda County | County Administration | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Board President | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Board Vice President | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | County Administrator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | County Clerk Recorder | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Division Chief | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | Division Chief of Operations/ Emergency Management | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | EMS Disaster and WMD Coordinator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Emergency Preparedness Manager | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Fire Chief | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | General | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | Main Line | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | OES Capt | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | OES EOC Lead | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | President of the Board | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Safety & Emergency Preparedness Manager | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Senior Emergency Services Coordinator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Sheriff | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Superintendent of Water Distribution | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Supervisor | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Technician | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County | Train Ops | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | Watch Commander | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Alameda County | Water Operations Manager | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County CCA | General | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Alameda County Communication Facility | AT&T Services Inc | Tier 3 | 09/28/2024 04:38 PDT
Alameda County Communication Facility | Clearview Systems Inc | Tier 2 | 09/28/2024 04:38 PDT
Alameda County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Alameda County Communication Facility | Verizon | Tier 2 | 09/28/2024 03:41 PDT
Alameda County Livermore | Chief of Police | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | City Manager | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Council Member | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Deputy City Manager | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Deputy Fire Chief | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Emergency Manager | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Mayor | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Police Chief | Tier 2 | 09/28/2024 03:37 PDT
Alameda County Livermore | Vice Mayor | Tier 2 | 09/28/2024 03:37 PDT
Butte County | County Administration | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Admin Analyst II | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Board Chair | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Chief | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Chief Administrative Officer | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | County Clerk-Recorder | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Deputy Chief | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Butte County | Director | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Division Chief | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | General | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | General Services Director | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Interim OEM Director | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Lieutenant | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Public Health Director | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Sergeant | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County | Supervisor | HFRA, Tier 1, Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Butte County Communication Facility | AT&T Mobility | Tier 3 | 09/28/2024 03:41 PDT
Butte County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 09/28/2024 03:41 PDT
Butte County Communication Facility | Comcast | Tier 3 | 09/28/2024 03:41 PDT
Butte County Communication Facility | Comcast Cable Communications Management, LLC | HFRA, Tier 3 | 09/28/2024 03:41 PDT
Butte County Communication Facility | Comcast Fresno LLC | HFRA, Tier 3 | 09/28/2024 03:41 PDT
Butte County Communication Facility | Comcast Inc | HFRA | 09/28/2024 03:41 PDT
Butte County Communication Facility | Gte Mobile Net of California LP | Tier 3 | 09/28/2024 03:41 PDT
Butte County Communication Facility | T-Mobile West LLC | Tier 3 | 09/28/2024 03:41 PDT
Butte County Emergency Services Facility | County of Butte | Tier 3 | 09/28/2024 03:41 PDT
Butte County Other Facility | California Department of Forestry | Tier 3 | 09/28/2024 03:41 PDT
Butte County Paradise | Fire Department | HFRA, Tier 1, Tier 3 | 09/28/2024 03:38 PDT
Butte County Paradise | Chief | HFRA, Tier 1, Tier 3 | 09/28/2024 03:38 PDT
Butte County Paradise | Council Member | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Councilman | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Councilmember | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Deputy Chief | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Division Chief | HFRA, Tier 1, Tier 3 | 09/28/2024 03:38 PDT
Butte County Paradise | Fire Prevention Inspector 2 | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | General | HFRA, Tier 1, Tier 3 | 09/28/2024 03:38 PDT
Butte County Paradise | Lieutenant | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Mayor | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Police Chief | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Town Clerk | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Paradise | Town Manager | HFRA, Tier 1, Tier 3 | 09/28/2024 03:37 PDT
Butte County Tribal | Chairwoman | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:29 PDT
Butte County Tribal | Director of Environmental Planning and Protection | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:29 PDT
Butte County Tribal | Executive Assistant | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:29 PDT
Butte County Tribal | Land Manager | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:30 PDT
Butte County Tribal | Tribal Chairman | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:29 PDT
Butte County Tribal | Vice Chairwoman | HFRA, Tier 1, Tier 2, Tier 3 | 09/30/2024 16:29 PDT
Colusa County | Fire Department | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Board Chair | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | County Clerk/Recorder | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | County Supervisor | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Deputy Chief | HFRA, Tier 2 | 09/28/2024 03:38 PDT
Colusa County | Director | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Division Chief | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Emergency Service Technician | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | General | HFRA, Tier 2 | 09/28/2024 03:38 PDT
Colusa County | MHOAC | HFRA, Tier 2 | 09/28/2024 03:38 PDT
Colusa County | Sheriff | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Supervisor | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County | Vice Chair | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Colusa County Communication Facility | AT&T | Tier 2 | 09/28/2024 03:41 PDT
Colusa County Communication Facility | AT&T Mobility LLC | Tier 2 | 09/28/2024 03:41 PDT
Colusa County Communication Facility | AT&T Services Inc | Tier 2 | 09/28/2024 03:41 PDT
Colusa County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 09/28/2024 03:41 PDT
Colusa County Communication Facility | Gte Mobile Net of California LP | Tier 2 | 09/28/2024 03:41 PDT
Colusa County Emergency Services Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Colusa County Emergency Services Facility | County of Colusa | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Colusa County Emergency Services Facility | Indian Valley - Bear Valley Fire Protection Distri | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:42 PDT
Colusa County Emergency Services Facility | Indian Valley Fire Protection District | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:42 PDT
Colusa County Energy Sector Facility | City Of Santa Clara | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 14:22 PDT
Colusa County Energy Sector Facility | Western Area Power Administration | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Colusa County Water And Waste Water Facility | California Department Of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Colusa County Water And Waste Water Facility | County Of Colusa | Tier 2 | 09/28/2024 03:41 PDT
Contra Costa County | County Administrator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Board Chair | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Board Vice Chair | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Chair of the Board | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Chief of Staff | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | County Administrator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | County Clerk Recorder | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Deputy Fire Chief, Mutual Aid Coordinator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Duty Officer | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Duty Officer - 24/7 Staff call line | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Emergency Manager | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Emergency Preparedness Manager | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Contra Costa County | Fire Chief | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | OES Warning System | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Sheriff | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County | Supervisor | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County Communication Facility | AT&T Services Inc | Tier 3 | 09/28/2024 03:41 PDT
Contra Costa County Communication Facility | County Of Contra Costa | Tier 3 | 09/28/2024 03:41 PDT
Contra Costa County Communication Facility | US Coast Guard | Tier 3 | 09/28/2024 03:41 PDT
Contra Costa County Emergency Services Facility | San Ramon Valley Fire District | Tier 3 | 09/28/2024 03:41 PDT
Contra Costa County CCA | General | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Contra Costa County Tribal | Chairperson | Tier 2, Tier 3 | 09/30/2024 14:17 PDT
Contra Costa County Tribal | Tribal Administrator | Tier 2, Tier 3 | 09/30/2024 14:17 PDT
Glenn County | CAO | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | County Administrative Officer | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | Deputy Director OES | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | Director of Public Works Agency | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | Fire Chief | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | General | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County | Sheriff | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Glenn County Communication Facility | American Tower Corporation | Tier 2 | 09/28/2024 03:41 PDT
Glenn County Communication Facility | AT&T Services Inc | HFRA, Tier 2 | 09/28/2024 03:41 PDT
Glenn County Communication Facility | Gte Mobile Net of California LP | HFRA | 09/28/2024 03:41 PDT
Glenn County Communication Facility | Verizon | Tier 2 | 09/28/2024 03:41 PDT
Glenn County Emergency Services Facility | County of Glenn | Tier 2 | 09/28/2024 03:41 PDT
Glenn County Emergency Services Facility | Elk Creek Fire District | Tier 2 | 09/28/2024 14:22 PDT
Glenn County Energy Sector Facility | City of Santa Clara | HFRA | 09/29/2024 10:44 PDT
Glenn County Orland | City Clerk | HFRA, Tier 2 | 09/29/2024 10:40 PDT
Glenn County Orland | City Manager | HFRA, Tier 2 | 09/29/2024 10:40 PDT
Glenn County Orland | Fire Chief | HFRA, Tier 2 | 09/29/2024 10:40 PDT
Glenn County Orland | General | HFRA, Tier 2 | 09/29/2024 10:41 PDT
Glenn County Orland | Public Works Director | HFRA, Tier 2 | 09/29/2024 10:40 PDT
Glenn County Other Facility | US Army Corps Of Engineers | HFRA | 09/28/2024 03:41 PDT
Glenn County Water And Waste Water Facility | Elk Creek Community Service | Tier 2 | 09/28/2024 14:22 PDT
Glenn County Water And Waste Water Facility | US Army Corps Of Engineers | HFRA | 09/29/2024 10:44 PDT
Glenn County Tribal | Interim Tribal Secretary | HFRA, Tier 2 | 09/28/2024 14:35 PDT
Glenn County Tribal | Tribal Administrator | HFRA, Tier 2 | 09/28/2024 14:35 PDT
Humboldt County | 1st District County Supervisor | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Board of Supervisors | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Corrections Lieutenant | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Executive Assistant | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Field Representative | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Fire Chief | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | MHOAC | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | OES Director | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Operations Lieutenant | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Senior Environmental Analyst | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Sheriff | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | State Senator | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Supervisor | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County | Unit Chief | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Humboldt County CCA | General | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Napa County | County Administration | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Board Chair | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | County Clerk/Recorder | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Emergency Services Officer | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Fire Chief | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | GIS | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | General | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Interim County Executive Officer | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | MHOAC | Tier 3, Tier 2 | 09/28/2024 03:38 PDT
Napa County | Sheriff | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Supervisor | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County | Under-Sheriff | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Napa County Communication Facility | AT&T Mobility LLC | Tier 3, Tier 2 | 09/28/2024 03:41 PDT
Napa County Communication Facility | California Highway Patrol | Tier 2 | 09/28/2024 03:41 PDT
Napa County Communication Facility | T-Mobile West Corporation | Tier 3 | 09/28/2024 03:41 PDT
Napa County CCA | General | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
San Luis Obispo County | Duty Chief | Tier 3, Tier 2 | 09/28/2024 03:38 PDT
San Luis Obispo County | Duty Officer | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
San Luis Obispo County | Emergency Services Manager | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
San Luis Obispo County | Fire Chief | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
San Luis Obispo County | General | Tier 3, Tier 2 | 09/28/2024 03:38 PDT
San Luis Obispo County | OES Duty Officer | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
San Luis Obispo County | Watch Commander | Tier 3, Tier 2 | 09/28/2024 03:38 PDT
San Luis Obispo County CCA | General | Tier 3, Tier 2 | 09/28/2024 03:37 PDT
Santa Barbara County | Fire Chief | Tier 3 | 09/28/2024 03:37 PDT
Santa Barbara County | OEM Duty Officer | Tier 3 | 09/28/2024 03:37 PDT
Santa Barbara County | OES Director | Tier 3 | 09/28/2024 03:37 PDT
Santa Barbara County | Sheriff | Tier 3 | 09/28/2024 03:37 PDT
Santa Barbara County Communication Facility | Frontier Communications Corporation Dip | Tier 3 | 09/28/2024 03:41 PDT
Santa Barbara County CCA | General | Tier 3 | 09/28/2024 03:37 PDT
Shasta County | EMS | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Fire Chief | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | General | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Interim Tribal Administrator | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Shasta County | Lieutenant | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Office of Emergency Services Coordinator | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Shasta County | Operations Manager | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Sergeant | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Sheriff-Coroner | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Staff Chief, Northern Operations | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County | Tribal Chairman | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Shasta County Anderson | Chief Plant Operator (Wastewater treatment plant) | Tier 2 | 09/28/2024 03:37 PDT
Shasta County Anderson | City Manager | Tier 2 | 09/28/2024 03:37 PDT
Shasta County Anderson | Deputy Public Works Director | Tier 2 | 09/28/2024 03:37 PDT
Shasta County Anderson | Fire Chief | Tier 2 | 09/28/2024 03:37 PDT
Shasta County Communication Facility | AT&T | Tier 3 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | AT&T Mobility LLC | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Charter Communications Holding Company Llc | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Cingular Wireless Services, Inc | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Frontier Communications Corporation Dip | Tier 3, Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Happy Valley Telephone Co | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Metro Pcs Inc | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Sprint Corporation | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | TDS Telecom | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | US Department of Agriculture | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Verizon | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Communication Facility | Verizon Wireless | Tier 3 | 09/28/2024 03:41 PDT
Shasta County Emergency Services Facility | California Department of Forestry | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Emergency Services Facility | County of Shasta | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Emergency Services Facility | Happy Valley Fire Protection District | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Emergency Services Facility | US Department of Agriculture | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Other Facility | California Department of Forestry | Tier 2 | 09/28/2024 03:41 PDT
Shasta County Other Facility | Happy Valley Telephone Co | Non-HFTD or Non-HFRA; within PSPS scope (see Footnote 1) | 09/28/2024 03:41 PDT
Shasta County Tribal | Tribal Administrator | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County Tribal | Administrative Assistant | Tier 2, Tier 3 | 09/30/2024 16:23 PDT
Shasta County Tribal | Interim Tribal Administrator | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Shasta County Tribal | Maintenance Supervisor | Tier 2, Tier 3 | 09/30/2024 16:23 PDT
Shasta County Tribal | OES Director | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Shasta County Tribal | Office of Emergency Services Coordinator | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Shasta County Tribal | Senior Director | Tier 2, Tier 3 | 09/30/2024 16:23 PDT
Shasta County Tribal | Tribal Chairman | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | County Administration | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | 1st District Sonoma County Supervisor | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Sonoma County | Board Chair | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Board Vice Chair | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Community Alert & Warning Manager | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Sonoma County | Deputy Director | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Director | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Division Chief | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | EMS | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | EMS Dispatch | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Fire Captain | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | MHOAC | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Main Office | Tier 2, Tier 3 | 09/28/2024 03:38 PDT
Sonoma County | Sheriff | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Sheriff Dispatch | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Sheriff's Liaison | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Staff Duty Officer | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County | Supervisor | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County Communication Facility | Comcast Fresno LLC | Tier 3 | 09/28/2024 03:41 PDT
Sonoma County CCA | General | Tier 2, Tier 3 | 09/28/2024 03:37 PDT
Sonoma County Tribal | Chairman | Tier 2, Tier 3 | 10/01/2024 09:32 PDT
Sonoma County Tribal | Chairperson | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Sonoma County Tribal | Grants Administrator | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Sonoma County Tribal | TANF Director | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Sonoma County Tribal | Tribal Administrator | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Sonoma County Tribal | Tribal Preservation Officer | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Sonoma County Tribal | Vice Chairperson | Tier 2, Tier 3 | 10/01/2024 09:31 PDT
Tehama County | Chief Administrator | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County | Communications Supervisor | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County | County Clerk / Recorder | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County | Lieutenant and OES manager | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County | OES Director | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County | Sheriff | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Tehama County Communication Facility | AT&T Mobility | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Communication Facility | AT&T Services Inc | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Communication Facility | Ducor Telephone Co | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Communication Facility | Ducor Telephone Corp | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Corning | City Clerk | Tier 2 | 09/28/2024 03:37 PDT
Tehama County Corning | City Manager | Tier 2 | 09/28/2024 03:37 PDT
Tehama County Corning | Police Chief | Tier 2 | 09/28/2024 03:37 PDT
Tehama County Emergency Services Facility | California Department of Forestry | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Government - Jail Facility | California Department of Corrections | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Other Facility | Burns, Sherri | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Other Facility | California Department of Forestry | Tier 2 | 09/28/2024 03:41 PDT
Tehama County Red Bluff | Chief of Police | Tier 2 | 09/28/2024 03:37 PDT
Tehama County Red Bluff | City Manager | Tier 2 | 09/28/2024 03:37 PDT
Trinity County | Deputy Director | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Trinity County | District Ranger, TRMU | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Trinity County | General | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Trinity County | Health Officer | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Trinity County | OES Manager | HFRA, Tier 2 | 09/28/2024 03:37 PDT
Trinity County Communication Facility | Frontier Communications Corporation Dip | HFRA, Tier 2 | 09/28/2024 03:41 PDT
1 Catastrophic Fire Behavior runs both in and outside of High Fire Risk Areas (HFRA). The PG&E Meteorology Team evaluates non-HFRA areas for catastrophic wildfire risk in unusual circumstances.

## Table F-1
Table F-1. Community Resource Centers Provided by PG&E
# | County | Site Name | Address | Operating Hours (PDT) |  | Total Visitors | Indoor / Outdoor | Amenities Provided
|  |  |  | Day 1 | Day 2
|  |  |  | 2024-09-30 | 2024-10-01
1 | Butte | Concow Elementary School | 11679 Nelson Bar Rd | 8:00 – 22:00 | 8:00 – 9:30 | 12 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
2 | Colusa | Stonyford Community Hall | 229 Market St | 8:00 – 15:00 | No | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
3 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309 | 8:00 – 20:00 | No | 35 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
4 | Glenn | Orland Shopping Center | 1016 South St | 8:00 – 18:30 | No | 23 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
5 | Napa | Calistoga Community Center | 1307 Washington Street | 8:00 – 22:00 | 8:00 – 9:30 | 25 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
6 | Shasta | Frontier Senior Center | 2081 Frontier Trail | 8:00 – 20:00 | No | 29 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
7 | Shasta | Dignity Health Mercy Oaks | 100 Mercy Oaks Dr | 8:00 – 21:00 | No | 28 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
8 | Shasta | Hill Country Health and Wellness Center | 29632 CA-299 | 8:00 – 22:00 | 8:00 – 12:00 | 129 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
9 | Tehama | Rancho Tehama Association | 17605 Park Terrace Road | 8:00 – 15:00 | No | 144 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
10 | Tehama | Lassen Mineral Lodge | 18961 Husky Way | 8:00 – 15:00 | No | 23 | Outdoor | *Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Cooling & Heating, Seating, Ice
11 | Trinity | Southern Trinity High School | 600 Van Duzen Rd | 8:00 – 20:00 | No | 6 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Device Charging, Medical Device Charging, Seating