## Table 1
Table 1: Customers Notified and De-energized
Total Customers4 |  |  | MBL Customers | Counties | Tribes | Circuits |  |  | Damage / Hazard Count | Critical Facilities and Infrastructure De-energized
Notified | De-energized | Cancelled | De-energized | De-energized | De-energized | Transmission De-energized | Unique Distribution Circuits in Any Version of Scope | Distribution Circuits De-energized
12291 | 1843 | 10448 | 168 | 8 | 1 | 0 | 34 | 15 | 0 | 78
4 The "Total Number of Customers," based on SPIDs, does not include streetlights.

## Table 2
Table 2: PSPS Risk-Benefit Consequence Modeling Considerations
Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS events and other large external outage events.6
Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.7 | Calculated based on two financial estimates 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.8
6 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
7 See A.20-06-012.
8 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
Table 3: Notification Descriptions
Type of Notification | Recipients | Description
PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs16 | On June 29, 2024, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E is monitoring an increased potential of PSPS outages. Following PG&E’s activation of its EOC, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS. • PG&E sent notifications to other Public Safety Partners via call, text and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When weather is anticipated to pass.
o Estimated Time of Restoration (ETOR).
o Links to the PSPS Portal where event-specific maps and information are available.
• Local PG&E representatives called potentially impacted County OES and select Tribes to inform them that PG&E is monitoring an increased potential of PSPS.
WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers), | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES. • PG&E sent notifications to other Public Safety Partners, and all customers via call, text message and e-mail; these notifications included the following information:
o Estimated window of the de-energization time.
o When the adverse weather is anticipated to pass.
o Estimated window of the de-energization time.
o ETOR.
o For Public Safety Partners only: Links to the PSPS Portal.
o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL program, language support, and the Portable Battery Program.
• PG&E sent notifications to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to get PSPS information in 15 non-English languages, referred to herein as “translated languages.” Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL program | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications to other Public Safety Partners, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.” • PG&E sent notifications to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would be shut off. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers) | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E sent notification to other Public Safety Partners and customers via call, text messages, and e-mail, which included:
o Impacted addresses (for customers only).
o De-energization time.
o When the adverse weather is anticipated to pass.
o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL program, Meals on Wheels, language support, and the Portable Battery Program.
Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers) | After the weather event had passed and the area is deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include:
o New field or meteorology conditions.
o Damage was found during patrols and repair is needed.
Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers) | Once customers, including MBL program customers and SIV customers, were restored, they received notifications via call, text and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text and e-mail. Public Safety Partner notifications were provided in English.
16 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a community resource center during a proactive de-energization event. Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly-owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.

## Table 4
Table 4: Customer Notification Timeline Summary
Event Order | Minimum Timeline19 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Who made the Notification
Pre-De-energization (Prior) | 72-48 hours | Tribal/Local Governments and CCAs* | 6/29/2024 9:06 PM | Priority |  | PG&E
|  | Public Safety Partners** | 6/29/2024 8:51 PM | Priority |  | PG&E
| 48-24 hours | Tribal/Local Governments and CCAs* | 6/30/2024 4:56 PM | Watch |  | PG&E
|  | Public Safety Partners** | 6/30/2024 5:04 PM | Watch |  | PG&E
|  | All Customers*** | 6/30/2024 4:59 PM | Watch |  | PG&E
| 24-12 hours | Tribal/Local Governments and CCAs* | 7/1/2024 12:47 PM | Watch |  | PG&E
|  | Tribal/Local Governments and CCAs* | 7/01/2024 9:01 PM | Watch |  | PG&E
|  | Public Safety Partners** | 7/1/2024 12:19 PM | Watch |  | PG&E
|  | All Customers*** | 7/1/2024 12:17 PM | Watch |  | PG&E
|  | Public Safety Partners** | 7/1/2024 9:09 PM | Watch |  | PG&E
|  | All Customers*** | 7/1/2024 9:07 PM | Watch |  | PG&E
| 4-1 hours | Tribal/Local Governments and CCAs* | 7/2/2024 12:06 AM | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs | 7/2/2024 1:30 AM | Warning |  | PG&E
|  | Public Safety Partners** | 7/2/2024 11:59 PM | Warning |  | PG&E
|  | All Customers*** | 7/1/2024 11:58 PM | Warning |  | PG&E
|  | Public Safety Partners** | 7/2/2024 12:02 AM | Warning |  | PG&E
|  | All Customers*** | 7/2/2024 12:01 AM | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 7/2/2024 1:19 PM | Delay |  | PG&E
|  | Public Safety Partners** | 7/2/2024 1:20 PM | Delay |  | PG&E
|  | All Customers*** | 7/2/2024 1:20 PM | Delay |  | PG&E
Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 7/2/2024 4:15 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 4:46 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 4:53 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 5:03 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 5:22 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 5:42 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/2/2024 6:04 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 12:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 12:16 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 12:31 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 12:45 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 1:16 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 1:31 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 1:45 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 2:01 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 2:16 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 7/3/2024 6:31 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 4:15 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 4:46 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 4:53 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 5:03 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 5:22 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 5:42 AM | Power Off |  | PG&E
|  | All Customers*** | 7/2/2024 6:04 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 12:00 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 12:16 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 12:31 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 12:45 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 1:16 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 1:31 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 1:45 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 2:01 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 2:16 AM | Power Off |  | PG&E
|  | All Customers*** | 7/3/2024 6:31 AM | Power Off |  | PG&E
| Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 7/2/2024 4:07 PM | Inspecting/Weather All-Clear | First All-Clear Notification Sent | PG&E
|  | Tribal/Local Governments and CCAs* | 7/2/2024 4:22 PM | Inspecting/Weather All-Clear | First All- Clear Notification Sent | PG&E
|  | Tribal/Local Governments and CCAs* | 7/3/2024 3:12 PM | Inspecting/Weather All-Clear | Last All- Clear Notification Sent | PG&E
|  | Public Safety Partners** | 7/2/2024 12:18 PM | Inspecting/Weather All-Clear | First All- Clear Notification Sent | PG&E
|  | Public Safety Partners** | 7/3/2024 1:36 PM | Inspecting/Weather All-Clear | Last All- Clear Notification Sent | PG&E
|  | All Customers*** | 7/2/2024 12:18 PM | Inspecting/Weather All-Clear | First All Clear Notification Sent | PG&E
|  | All Customers*** | 7/3/2024 1:36 PM | Inspecting/Weather All-Clear | Last All Clear Notification Sent | PG&E
|  | Public Safety Partners** | 7/2/2024 1:51 PM | ETOR Update | First ETOR Update Notification Sent | PG&E
|  | Public Safety Partners** | 7/3/2024 5:35 PM | ETOR Update | Last ETOR Update Notification Sent | PG&E
|  | All Customers*** | 7/2/2024 1:51 PM | ETOR Update | First ETOR Update Notification Sent | PG&E
|  | All Customers*** | 7/3/2024 5:35 PM | ETOR Update | Last ETOR Update Notification Sent | PG&E
Restoration (After) | After re-energization | Tribal/Local Governments and CCAs* | 7/3/2024 8:50 PM | Restore |  | PG&E
|  | Public Safety Partners** | 7/2/2024 1:45 PM | Restore | First initial Restoration Notification sent. | PG&E
|  | Public Safety Partners** | 7/3/2024 7:22 PM | Restore | Last initial Restoration Notification sent. | PG&E
|  | All Customers*** | 7/2/2024 1:45 PM | Restore | First Restoration Notification sent. | PG&E
|  | All Customers*** | 7/3/2024 7:22 PM | Restore | Last Restoration Notification sent. | PG&E
Cancellation | Cancellation within 2-hours of decision to cancel **** | Tribal/Local Governments and CCAs* | 7/03/2024 2:58 PM | Cancel | Only Tribal/Local Governments and CCAs removed from scope received cancel notification. The decision to descope these customers was 7/3/2024 2:29 PM. | PG&E
|  | Public Safety Partners** | 7/3/2024 3:13 PM | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was 7/3/2024 2:29 PM. | PG&E
|  | All Customers*** | 7/3/2024 3:13 PM | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was 7/3/2024 2:29 PM. | PG&E
Ad-Hoc Notification | N/A | Delayed Customers | 7/2/2024 9:52 PM | Ad Hoc | Only customers delayed received this ad hoc notification. | PG&E
|  | Previously De-Energized Customers | 7/2/2024 10:22 PM | Ad Hoc | Only customers previously de-energized received this ad hoc notification. | PG&E
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators.
**A subset of Public Safety Partners, including water, wastewater, and communication service providers.
***All Customers, including MBL program customers and SIV customers.
20 Decision 19-05-042, Appendix A, Timing of Notification.

## Table 5
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted20
Designation | Total Number of customers21 | Notification Attempts Made22 | Timing of Attempts23 | Who made the Notification Attempt | Successful Positive Notification24
MBL25 | 1,143 26 | 1,142 Watch Notifications | 06/30/2024 5:00 PM PDT | PG&E | 1,100 Watch Notifications
|  | 1,142 Warning Notifications | 07/01/2024 10:36 AM PDT |  | 767 Warning Notifications
|  | 2,284 Overall Notifications | 06/30/2024 5:00 PM PDT |  | 1,867 Overall Notifications
MBL behind a master meter27 | 0 | 0 Watch Notifications | N/A | PG&E | 0 Watch Notifications
|  | 0 Warning Notifications | N/A |  | 0 Warning Notifications
|  | 0 Overall Notifications | N/A |  | 0 Overall Notifications
SIV | 328 | 327 Watch Notifications | 06/30/2024 5:02 PM PDT | PG&E | 304 Watch Notifications
|  | 327 Warning Notifications | 07/01/2024 10:16 AM PDT |  | 212 Warning Notifications
|  | 654 Overall Notifications | 06/30/2024 5:02 PM PDT |  | 516 Overall Notifications
20 Counts of Notification Attempts Made will not reflect the actual total of customers notified as both MBL and SIV customers can appear in both subset groups.
21 Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
22 Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
23 Initial start time notification was sent.
24 PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
25 Residential tenants of master-metered customers can also qualify for Medical Baseline quantities. The Medical Baseline category for the purposes of Table 5 does not include MBL program customers who are master meter tenants.
26 The "Total Number of Customers," based on SPIDs, does not include streetlights.
27 PG&E has additional processes in place to ensure MBL customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 6
Table 6: Outcomes of Notifications to De-energized Medical Baseline Program Customers
Count | Type of Notifications to De-energized MBL Customers (based on SPID) | Description
168 | Total De-energized MBL Program Customers | The number of customers de-energized who participate in PG&E’s MBL Program
168 | Total Notifications Attempted / Sent | The total sum of automated notifications attempted via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls.
0 | Total Notifications Not Attempted / Sent | Total MBL program customers de-energized that PG&E did not attempt to notify.
168 | Total Notifications Delivered | The total sum of automated notifications sent via call, text, and e-mail.
0 | Total Notifications Not Delivered | Total MBL program customers de-energized whose notification was not delivered.
144 | Total Notifications Initially Acknowledged | The total sum of automated notifications sent via call, text and email where notification was acknowledged.
54 | Total In-Person Visits/Doorbell Rings and Live Agent Phone Calls | Total attempted doorbell ring for impacted MBL program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.30 This includes call attempts made by Live Agent representatives to MBL program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit. Refer to Table 7 for the detailed breakdown of this category.
165 | Total Notifications Received | Customers who acknowledged their notification by taking one of the following actions: answered an automated or Live Agent phone call, responded to a text message, opened an e-mail, or greeted an in-person doorbell ring (excludes voicemails left, text message delivered only and not confirmed, door hanger left).
3 | Total Notifications Not Received | Total MBL program customers who did not confirm receipt / acknowledge their automated notifications, Live Agent phone calls or in-person doorbell ring. Customers who did not answer a doorbell ring were left a door hanger.
30 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 7
Table 7: Count and Type of Additional Notifications to De-energized Medical Baseline Program Customers
Count | Type of Additional Notifications to Impacted Medical Baseline Customers (based on SPID) | Description
26 | Total In-Person Visits / Doorbell Rings | Doorbell ring attempts to impacted MBL program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.31
28 | Live Agent Phone Calls | Calls made by Live Agent representatives to MBL program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit.
31 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 8
Table 8: Notification Failure Causes
Notifications Sent to | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
Public Safety Partners excluding Critical Facilities and Infrastructure35 | Entities who did not receive 48-to 72-hour priority notification | 0 | No failures.
| Entities who did not receive 1–4-hour imminent notification | 8 | A manual error in transferring data files that resulted in missed 1-4 hour notifications for eight Public Safety Partners. PG&E will ensure that those responsible for preparing these notification files have an awareness of the potential technological errors that may occur during this process.
| Entities who did not receive any notifications before de-energization | 0 | No failures.
| Entities who were not notified immediately before re-energization | 0 | No failures.
| Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
Critical Facilities and Infrastructure36 | Facilities who did not receive 1–4-hour imminent notification | 13 | See Table 8B for exaplanation.
| Facilities who did not receive any notifications before de-energization | 0 | No failures.
| Facilities who were not notified at de-energization | 46 | See Table 8D for explanation.
| Facilities who were not notified immediately before re-energization | 9 | See Table 8E for explanation.
| Facilities who were not notified when re-energization is complete | 9 | See Table 8F for explanation.
| Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
All other affected customers | Customers who did not receive 24–48-hour advance notifications | 1 | See Table 8A for explanation.
| Customers who did not receive 1–4-hour imminent notifications | 45 | See Table 8B for explanation.
| Customers who did not receive any notifications before de-energization | 1 | See Table 8C for explanation.
| Customers who were not notified at de-energization initiation | 699 | See Table 8D for explanation.
| Customers who were not notified immediately before re-energization | 30 | See Table 8E for explanation.
| Customers who were not notified when re-energization is complete | 15 | See Table 8F for explanation.
| Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.

## Table 8A
Table 8A: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who did not Receive 24-48 Hour Advance Notifications
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
0 | 1 (no MBL) | This customer was not notified prior to de-energization because the customer was not mapped due to a transformer mis-assignment. A mapping correction is being processed to fix the error.

## Table 8B
Table 8B: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who did not Receive 1-4 Hour Imminent Notifications
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
12 | 44 (4 MBL) | Due to scope and timing changes, staging and execution of Warning notification batches were incorrectly timed which caused some delayed Warning notifications to customers. See Section 11.2 for more information.
1 | 0 | This customer was not in the PSPS scope or notification file as the customer’s data was not associated with the circuit. A mapping correction is being processed to fix the error.
0 | 1 (no MBL) | This customer was not notified prior to de-energization because the customer was not mapped due to a transformer mis-assignment. A mapping correction is being processed to fix the error.

## Table 8C
Table 8C: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who did not Receive Any Notifications Before De-Energization
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
0 | 1 (no MBL) | This customer was not notified prior to de-energization because the customer was not mapped due to a transformer mis-assignment. A mapping correction is being processed to fix the error.

## Table 8D
Table 8D: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who were not notified of PowerOff at de-energization initiation
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
6 | 169 (13 MBL)34 | These customers received a delayed Power Off notification.35 A root cause is still being investigated and we will report our findings in the 2024 PSPS Post-Season Report.
1 | 0 | This customer was not in the PSPS scope or notification file as the customer’s data was not associated with the circuit. A mapping correction is being processed to fix the error.
1 | 2 (no MBL) | Our internal data platform incorrectly categorized this facility as not in service. A mapping correction is being processed to fix the error.
38 | 544 (38 MBL)36 | These customers did not receive a Power Off notification. A root cause is still being investigated and we will report our findings in the 2024 PSPS Post-Season Report.
34Explanation for customers who did not receive a Power Off notification during the first wave of de-energization, may differ for customers who did not receive Power Off notification for the second wave of de-energization. As a result, non-critical customer counts will not equal the total count of unique non-critical customers for missed Power Off notifications.
35 PG&E defines a “delayed” Power Off notification as a notification delivered more than two hours after the de-energization start based on average processing time.
36 Explanation for customers who did not receive a Power Off notification during the first wave of de-energization, may differ for customers who did not receive Power Off notification for the second wave of de-energization. As a result, non-critical customer counts will not equal the total count of unique non-critical customers for missed Power Off notifications.

## Table 8E
Table 8E: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who were not notified immediately before re-energization
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
7 | 22 (1 MBL) | These customers received an Inspect (All-Clear) notification after being restored. A root cause is still being investigated and we will report our findings in the 2024 PSPS Post-Season Report.
1 | 0 | This customer was not in the PSPS scope or notification file as the customer’s data was not associated with the circuit. A mapping correction is being processed to fix the error.
1 | 2 (no MBL) | Our internal data platform incorrectly categorized this facility as not in service. A mapping correction is being processed to fix the error.
0 | 6 (no MBL) | These customers did not receive Inspect (All-Clear) notification. A root cause is still being investigated and we will report our findings in the 2024 PSPS Post-Season Report.

## Table 8F
Table 8F: Explanation of Failures for Critical Facility and Infrastructure Customers and All Other Affected Customers who were not notified when re-energization is complete.
Count of Critical Facilities | Count of All Other Affected Customers | Explanation
1 | 0 | This customer was not in the PSPS scope or notification file as the customer’s data was not associated with the circuit. A mapping correction is being processed to fix the error.
1 | 2 (no MBL) | Our internal data platform incorrectly categorized this facility as not in service. A mapping correction is being processed to fix the error.
7 | 13 (no MBL) | A root cause is still being investigated and we will report our findings in the 2024 PSPS Post-Season Report.

## Table 9
Table 9: PSPS Portal Time & Date for Map Sharing
Date | Time PDF and GIS Maps Shared (PDT)
2024-06-29 | 20:32
2024-06-30 | 15:35
07/01/2024 | 11:34
07/01/2024 | 20:32
07/03/2024 | 14:47

## Table 10
Table 10: PSPS Notifications Submitted to Cal OES
Date | Time PDF and GIS Maps Shared
2024-06-29 | 21:14 PDT
2024-06-30 | 07:05 PDT
2024-06-30 | 14:58 PDT
2024-07-01 | 11:12 PDT
2024-07-01 | 12:42 PDT
2024-07-01 | 22:05 PDT
2024-07-02 | 00:44 PDT
2024-07-02 | 02:13 PDT
2024-07-02 | 03:15 PDT
2024-07-02 | 04:31 PDT
2024-07-02 | 05:34 PDT
2024-07-02 | 07:44 PDT
2024-07-02 | 12:57 PDT
2024-07-02 | 14:52 PDT
2024-07-03 | 00:32 PDT
2024-07-03 | 01:29 PDT
2024-07-03 | 02:02 PDT
2024-07-03 | 06:41 PDT
2024-07-03 | 11:27 PDT
2024-07-03 | 14:57 PDT
2024-07-03 | 20:03 PDT

## Table 11
Table 11: PSPS Notifications Submitted to Cal CPUC
Date | Time PDF and GIS Maps Shared
2024-06-29 | 18:59 PDT
2024-07-01 | 09:55 PDT
2024-07-01 | 18:36 PDT
2024-07-01 | 22:14 PDT
2024-07-02 | 00:28 PDT
2024-07-02 | 15:06 PDT
2024-07-03 | 01:08 PDT
2024-07-03 | 01:55 PDT
2024-07-03 | 13:37 PDT
2024-07-03 | 17:53 PDT
2024-07-03 | 20:00 PDT
2024-07-04 | 12:28 PDT

## Table 12
Table 12: Customer Notifications Based on Language Preference
Language | Total Notifications48 | Percent
English | 634729 | 99.06%
Spanish | 5454 | 0.85%
Chinese (Mandarin & Cantonese) | 502 | 0.08%
Vietnamese | 52 | 0.01%
Total | 640737 | 100%
48 Total notifications do not include doorbell rings and Live Agent phone calls.

## Table 13
Table 13: Call Center Support Services49
Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls (seconds) | Number of calls handled by Call Center Translation Services | Number of languages Supported by Call Center Translation Services
75492 | 2185 | 14 | 2182 | 240
49 Metrics are provided from June 29, 2024 through July 3, 2024.

## Table 14
Table 14: Generators Available for Critical Facilities and Infrastructure Customers
Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)51 | Description
Diesel Generator | 2 | 0.032 | 31 | 2 units on reserve in Sacramento.
Diesel Generator | 4 | 0.1 | 27 | 3 units on reserve in Sacramento.
Diesel Generator | 1 | 0.125 | 24 | 1 unit on reserve in San Leandro.
Diesel Generator | 5 | 0.2 | 24 | 4 units on reserve in San Leandro, one unit reserved in Sacramento.
Diesel Generator | 1 | 0.275 | 22 | 1 unit on reserve in Sacramento.
Diesel Generator | 1 | 0.57 | 24 | 1 unit on reserve in San Leandro.
Diesel Generator | 8 | 1 | 31 | 3 units pre-staged at one ICU Hospital. 5 on reserve at Sacramento.
Diesel Generator | 5 | 1.14 | 22 | 5 on reserve in San Leandro.
Diesel Generator | 12 | 2 | 35 | 9 units on reserve in San Leandro and three on reserve in Sacramento.
51 50,000 customer minutes is approximately equivalent to 100 customers for about 8 hours.

## Table 15
Table 15: Critical Facility and Infrastructure Customers Energized with Backup Generation
County | Site Type | Generation Deployed | Duration of Operation | Reason Deployed
Glenn | Elk Creek Community Water District | 0.230 MW | 0 hours | High risk to environment or Public Safety
Colusa | Cortina Rancheria Indian Reservation Residence | 0.07 MW | 62:05 hours | Health and Safety risk for Tribal elders
Colusa | Cortina Rancheria Indian Reservation Residence | 0.07 MW | 62:25 hours | Health and Safety risk for Tribal elders
Colusa | Cortina Rancheria Indian Reservation Residence | 0.07 MW | 62:10 hours | Health and Safety risk for Tribal elders
Shasta | CALFIRE Happy Valley Fire Center | 0.56 MW | 0 hours | High risk to environment or Public Safety

## Table 16
Table 16: Number and Nature of Complaints due to the July 2 – 3, 2024 PSPS
Nature of Complaints | Number of Complaints
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 30
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 14
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 37
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 53
Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 5

## Table 17
Table 17: Count and Type of Claim(s) Received
Description of Claims | Number of Claims
Business Interruption / Economic Loss | 1
Food Loss Only | 2
Property Damage | 0

## Table 18
Table 18: Weather All-Clear Times54
All-Clear Zones | Weather All-Clear Date and Time
170A, 175F, 177B, 245B, 246B | 07/02/2024 11:07
175D, 175E, 175G, 175H, 177C, 248A, 280C, 280G, 280H | 07/02/2024 12:23
175E, 177C, 280C, 280G | 07/03/2024 10:39
175F, 175H, 177B | 07/03/2024 11:46
175G, 245B, 246B, 248A, 280H | 07/03/2024 12:43
54 Due to the two-wave de-energization, some zones were given “All-Clear” twice for the July 2 – 3, 2024 PSPS.

## Table 19
Table 19: Lessons Learned from the PSPS
Issue | Discussion | Resolution
Customer Notification | A customer was incorrectly mapped which resulted in missed notifications. | Correct the customer's mapping to prevent future missed notifications and continue to refine our process.
Scope | Opportunity to re-energize customers within a PSPS. | PG&E re-energized customers during the afternoon and evening of July 2 when weather improved during the forecasted PSPS.
Customer Notification | Due to scope and timing changes, staging and execution of Warning notification batches were incorrectly timed which caused some missed Warning notifications to customers. | Internal data platforms did not identify the need to separate TP's into two separate batches based on de-energization time. PG&E plans to evaluate our internal processes and data systems to ensure appropriate notification timing is met.

## Table 20
Table 20: Maximum Wind Gusts Recorded July 2 - 3, 2024 in Impacted Counties
County | Maximum Wind Gust (mph) | Station ID | Station Name
Butte | 49 | JBGC1 | Jarbo Gap
Colusa | 35 | PG598 | Rail Canyon Road
Glenn | 40 | PG845 | Road 65
Lake | 45 | PG126 | Mt St Helena East
Napa | 42 | PG358 | Knoxville
Shasta | 44 | KRDD | Redding Municipal Airport
Solano | 43 | PG880 | Blue Ridge Road South
Sonoma | 49 | PG303 | Healdsburg Hills North
Tehama | 51 | 571PG | Round Mountain - Tehama
Yolo | 48 | PG490 | Bald Mountain Tower

## Table A-1.1
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the July 2 – 3, 2024 PSPS Event
| Time Place | Forecast | [18 empty] | Agency |  |  |  | Observed1
Circuit Name |  | ws_mph | ws_mph_ 50m | wg_ec_mph | temp_2m_ f | flame_length_ft_2hr | rate_of_spread_chhr_2hr | area_acres_ 8hr | rh_2m | vpd2m_mb | prob_cat | dfm_10hr | dfm_100 hr | dfm_1000 hr | lfm_herb | lfm_woody | lfm_ chamise_new | sum_tree_ovr | prob_ ignition | cfpd | HWW | HWA | RFW | GACC_High Risk | Observed ws_mph | Observed wg_ mph | Observed temp_f | Observed RH_% | Observed ws_mph_AC | Observed wg_mph_AC | Observed temp_f_AC | Observed RH_%_AC | open_psps_tags | Tx_impacts_yes_no | PSPS Potential Risk Consequence | PSPS Potential Benefit
ARBUCKLE 1101 | TP7 | 16 | 23 | 34 | 110 | 8 | 29.1 | 2033.9 | 4.2 | 85 | 0.912 | 0.017 | 0.041 | 0.058 | 43 | 85 | 87 | -99 | 0.0005807 | 3.7 | No | No | 714 | 714 | 17, 18 | 27, 26 | 93, 96 | 20, 13 | 14, 15 | 22, 22 | 94, 96 | 24, 18 | Yes | No | 0.07914 | 6.5
BIG BEND 1101 | TP11 | 19 | 30 | 44 | 107 | 9.1 | 38.7 | 2350.8 | 5.2 | 76.1 | 0.971 | 0.017 | 0.04 | 0.06 | 37 | 96 | 102 | 88659.2 | 0.0027847 | 21.9 | No | No | No | 120 | 29, 29 | 49, 46 | 99, 103 | 15, 12 | 12, 14 | 24, 21 | 99, 103 | 14, 12 | Yes | No | 0.28633 | 33.5
CALISTOGA 1101 | TP12 | 19 | 29 | 42 | 98 | 18.3 | 37.5 | 1308.2 | 7.8 | 56.7 | 0.944 | 0.026 | 0.05 | 0.068 | 71 | 87 | 93 | 62182.1 | 0.0007465 | 4.9 | No | No | 402 | 1696 | 49, 47 | 63, 64 | 100, 101 | 15, 9 | 13, 15 | 19 | 100 | 13 | Yes | No | 0.08254 | 49.5
CALPINE 1144 | TP12 | 17 | 27 | 40 | 104 | 10.4 | 45.3 | 1773.1 | 6.1 | 69 | 0.967 | 0.022 | 0.047 | 0.066 | 56 | 89 | 92 | 3736.7 | 0.0006404 | 3.7 | No | No | 17 | 17 | 42, 37 | 54, 47 | 112, 118 | 13, 8 | 17, 23 | 24, 30 | 110, 110 | 13, 9 | Yes | No | 0.08095 | 4.1
CALPINE 1146 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No | No | No | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes | No | N/A | N/A
CORNING 1101 | TP5 | 20 | 27 | 39 | 109 | 9.8 | 99.3 | 16936 | 3.9 | 81.4 | 0.939 | 0.018 | 0.042 | 0.058 | 34 | 97 | 92 | 6259.9 | 0.0007983 | 5.3 | No | No | 2224 | 2224 | 21, 24 | 32, 37 | 95, 96 | 19, 10 | 15, 21 | 27, 30 | 96, 98 | 18, 10 | Yes | No | 1.3914 | 184.9
CORNING 1102 | TP5 | 22 | 28 | 41 | 108 | 11 | 137.9 | 26758 | 3.8 | 80.7 | 0.993 | 0.017 | 0.039 | 0.055 | 34 | 82 | 92 | 1979 | 0.0005782 | 3.9 | No | No | 1703 | 1703 | 25, 33 | 36, 51 | 97, 100 | 13, 4 | 14, 23 | 25, 34 | 98, 100 | 15, 7 | Yes | No | 0.48068 | 122.9
CORTINA 1101 | TP7 | 17 | 25 | 33 | 108 | 9.5 | 42.6 | 3814.1 | 4.1 | 80.2 | 0.964 | 0.018 | 0.041 | 0.058 | 41 | 87 | 89 | 18.4 | 0.0003352 | 2.7 | No | No | 263 | 263 | 15, 14 | 23, 31 | 96, 100 | 17, 11 | 13, 14 | 20, 22 | 97, 100 | 15, 11 | Yes | No | 0.08274 | 7.5
DUNNIGAN 1103 | TP7 | 16 | 24 | 35 | 110 | 8.5 | 33.8 | 2610.4 | 4.3 | 85.3 | 0.947 | 0.017 | 0.042 | 0.058 | 39 | 86 | 88 | 477.9 | 0.0005215 | 4 | No | No | 308 | 308 | 17, 18 | 27, 26 | 93, 96 | 20, 13 | 14, 15 | 22, 22 | 94, 96 | 24, 18 | Yes | No | 0.08633 | 9.5
HIGHLANDS 1103 | TP8 | 20 | 31 | 46 | 105 | 11.1 | 48 | 4439.4 | 5.1 | 72.4 | 0.971 | 0.02 | 0.047 | 0.066 | 44 | 83 | 90 | 1149.6 | 0.0013107 | 7.8 | No | No | 2422 | 2422 | 27, 26 | 42, 41 | 97, 101 | 14, 9 | 18, 14 | 24, 24 | 98, 102 | 13, 9 | Yes | No | 0.11036 | 118.3
MADISON 2101 | TP7 | 21 | 34 | 43 | 111 | 8.6 | 62.6 | 5250.8 | 4.4 | 86.4 | 0.958 | 0.017 | 0.039 | 0.056 | 37 | 83 | 87 | 639.3 | 0.0011822 | 10.2 | No | No | 2184 | 2184 | 30, 31 | 47, 48 | 102, 102 | 13, 10 | 18, 15 | 26, 24 | 102, 101 | 13, 13 | Yes | No | 0.12943 | 75.4
MIDDLETOWN 1101 | TP12 | 22 | 32 | 47 | 104 | 12.4 | 34.2 | 1452.6 | 6.1 | 69 | 0.967 | 0.022 | 0.045 | 0.063 | 56 | 88 | 92 | 39459.6 | 0.0013731 | 9 | No | No | 2024 | 2103 | 49, 47 | 63, 64 | 112, 118 | 14, 9 | 17, 23 | 24, 30 | 110, 110 | 13, 9 | Yes | No | 0.16502 | 30.1
MONTICELLO 1101 3 | TP9 | 21 | 33 | 44 | 108 | 10.9 | 53.5 | 3924.2 | 5.1 | 79.9 | 0.977 | 0.021 | 0.048 | 0.068 | 37 | 85 | 88 | 264.8 | 0.0010168 | 8.3 | No | No | 1394 | 1412 | 21 | 35 | 100 | 15 | 12 | 22 | 101 | 15 | Yes | No | 0.08274 | 37.8
PUTAH CREEK 1102 | TP10 | 18 | 28 | 36 | 111 | 8.7 | 81.4 | 2133.5 | 4.9 | 86.7 | 0.934 | 0.018 | 0.041 | 0.056 | 40 | 89 | 88 | 4835.7 | 0.0006609 | 3.4 | No | No | 917 | 917 | 29, 25 | 43, 35 | 99, 98 | 16, 12 | 18, 18 | 25, 26 | 99, 99 | 17, 15 | Yes | No | 0.1984 | 67.7
VACAVILLE 1108 | TP10 | 21 | 31 | 43 | 109 | 6.6 | 24.6 | 1325.9 | 5.8 | 80.6 | 0.917 | 0.019 | 0.041 | 0.057 | 47 | 92 | 91 | 2154.1 | 0.0008325 | 5.3 | No | No | 2475 | 2476 | 29, 25 | 43, 35 | 111, 101 | 16, 12 | 16, 12 | 26, 21 | 104, 104 | 15, 13 | Yes | No | 0.11865 | 36.6
1 Wave 1 and wave 2 de-energization data is separated by comma in applicable fields.
2 PSPS decision-making and de-energization data was not calculated for the CALPINE 1146 circuit due to no customer impact.
3 Only the first wave of de-energization occurred for Monticello 1101.

## Table A-1.2
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the July 2 – 3, 2024 PSPS Event
Forecast / Agency / |  |  |  | Value Provided
Observed | Value | Name | Unit |  | Description
Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all- clear time.
Observed | Observed temp_f | Observed Temperature during Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
Observed | open_psps_tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags
(Priority A - emergency, B - urgent, and E/F - risk-based)
Observed | Tx_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de- energization of upstream transmission lines, regardless of
whether those distribution lines would have also been de- energized due to direct distribution PSPS.
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
Forecast | wg_ec_mph | Forecasted Peak Wind Gust | mph | max | Wind gust in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at two meters above ground level.
Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first two hours of fire spread simulation from Technosylva.
Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first two hours of fire spread simulation from Technosylva.
Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at two meters above ground level.
Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface.
Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of
the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
|  | Dead Fuel Moisture Content 1000 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_1000hr
Forecast | lfm_herb | Live Fuel Moisture Content-herbaceous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
Forecast | sum_tree_ovr | Tree Overstrike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
Forecast | prob_ignition | Ignition Probability Weather (IPW) Model Output | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an ourly basis
Forecast | cfpd | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is
called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.

## Table B-1
Table B-1: Circuits De-Energized During the July 2 – 3, 2024 PSPS Event
Distribution / Transmission | Circuit Name | De-Energization Date and Time | All-Clear Date and Time | Restoration Date and Time | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | Medical Baseline Customers | AFN other than MBL Customers | Other Customers
Distribution | ARBUCKLE 1101 | 2024-07-02 01:09 | 2024-07-03 11:46 | 2024-07-03 14:23 | COLUSA | Outside HFTD | 3 | 2 | 0 | 0 | 0 | 1
Distribution | BIG BEND 1101 | 2024-07-02 00:29 | 2024-07-03 12:43 | 2024-07-03 16:52 | BUTTE | Tier 3, Tier 2 | 277 | 250 | 25 | 27 | 86 | 2
Distribution | CALISTOGA 1101 | 2024-07-02 01:10 | 2024-07-03 12:43 | 2024-07-03 14:25 | NAPA | Tier 3 | 9 | 0 | 8 | 0 | 0 | 1
Distribution | CALPINE 1144 | 2024-07-02 01:37 | 2024-07-03 12:43 | 2024-07-03 17:54 | SONOMA, LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 15 | 2 | 13 | 0 | 0 | 0
Distribution | CALPINE 1146 | 2024-07-02 01:37 | 2024-07-03 12:43 | 2024-07-03 17:54 | LAKE | Outside HFTD | 1 | 0 | 1 | 0 | 0 | 0
Distribution | CORNING 1101 | 2024-07-02 04:42 | 2024-07-03 12:43 | 2024-07-03 17:56 | TEHAMA | Partially Outside HFTD, Tier 2 | 804 | 743 | 58 | 98 | 363 | 3
Distribution | CORNING 1102 | 2024-07-02 04:50 | 2024-07-03 12:43 | 2024-07-03 17:10 | TEHAMA | Partially Outside HFTD, Tier 2 | 247 | 200 | 40 | 18 | 67 | 7
Distribution | CORTINA 1101 | 2024-07-02 00:59 | 2024-07-03 11:46 | 2024-07-03 14:20 | COLUSA | Tier 2 | 8 | 3 | 5 | 0 | 0 | 0
Distribution | DUNNIGAN 1103 | 2024-07-02 00:57 | 2024-07-03 11:46 | 2024-07-03 14:20 | YOLO, COLUSA | Partially Outside HFTD, Tier 2 | 13 | 9 | 3 | 0 | 3 | 1
Distribution | HIGHLANDS 1103 | 2024-07-02 04:05 | 2024-07-03 11:46 | 2024-07-03 14:10 | LAKE | Partially Outside HFTD, Tier 2 | 49 | 34 | 11 | 3 | 10 | 4
Distribution | MADISON 2101 | 2024-07-02 01:00 | 2024-07-03 11:46 | 2024-07-03 14:16 | YOLO | Partially Outside HFTD, Tier 2 | 73 | 45 | 19 | 1 | 15 | 9
Distribution | MIDDLETOWN 1101 | 2024-07-02 01:14 | 2024-07-03 12:43 | 2024-07-03 14:01 | NAPA, SONOMA, LAKE | Tier 3 | 111 | 99 | 10 | 3 | 14 | 2
Distribution | MONTICELLO 1101 | 2024-07-02 01:54 | 2024-07-02 12:23 | 2024-07-02 15:04 | NAPA | Tier 2 | 8 | 0 | 7 | 0 | 0 | 1
Distribution | PUTAH CREEK 1102 | 2024-07-02 01:19 | 2024-07-03 11:46 | 2024-07-03 14:02 | YOLO, SOLANO | Partially Outside HFTD, Tier 2 | 169 | 126 | 32 | 16 | 12 | 11
Distribution | VACAVILLE 1108 | 2024-07-02 01:20 | 2024-07-03 10:39 | 2024-07-03 13:02 | NAPA, SOLANO | Partially Outside HFTD, Tier 2 | 56 | 26 | 25 | 2 | 4 | 5
Total | [6 empty] | 1843 | 1539 | 257 | 168 | 574 | 47

## Table C-1
Table C-1: Public Safety Partners Contacted
Organization/Jurisdiction | Title | HFTD or HFRA Tier | Date/Time Contacted
Butte County | County Administration | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County | Admin Analyst II | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Board Chair | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County | Chief | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Chief Administrative Officer | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County | County Clerk-Recorder | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Deputy Chief | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County | Deputy County Administrative Officer - Emergency Management | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Director | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Division Chief | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | General | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | General Services Director | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Lieutenant | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Probation Officer | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County | Public Health Director | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Senior Contracts/Procurement Agent and EOD Logistics Chief | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Sergeant | Tier 3, Tier 2 | 07/01/2024 12:32 PDT
Butte County | Supervisor | Tier 3, Tier 2 | 07/01/2024 12:47 PDT
Butte County Communication Facility | AT&T Mobility | Tier 3 | 07/01/2024 12:18 PDT
Butte County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 07/01/2024 12:18 PDT
Butte County Emergency Services Facility | County Of Butte | Tier 3 | 07/01/2024 12:51 PDT
Butte County Other Facility | California Department of Forestry | Tier 3 | 07/01/2024 12:18 PDT
Colusa County | Board Chair | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | County Clerk/Recorder | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | County Supervisor | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | Deputy Chief | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | Director | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | Division Chief | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | Emergency Service Technician | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | Fire Chief | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | General | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Colusa County | MHOAC | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | Sheriff | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | Supervisor | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County | Vice Chair | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Colusa County Tribal | Chairperson | Tier 2 | 06/29/2024 21:06 PDT
Colusa County Communication Facility | AT&T | Tier 2 | 06/29/2024 20:53 PDT
Colusa County Communication Facility | AT&T Mobility LLC | Tier 2 | 06/29/2024 20:53 PDT
Colusa County Communication Facility | AT&T Services Inc | Tier 2 | 06/29/2024 20:53 PDT
Colusa County Communication Facility | Citizens Telecommunications of California Inc. | Tier 2 | 06/29/2024 21:02 PDT
Colusa County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 06/29/2024 21:02 PDT
Colusa County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 06/29/2024 20:53 PDT
Colusa County Emergency Services Facility | California Department of Forestry | Tier 3, Tier 2 | 06/29/2024 21:02 PDT
Colusa County Emergency Services Facility | County Of Colusa | Tier 2 | 06/29/2024 21:02 PDT
Colusa County Energy Sector Facility | City Of Santa Clara | Tier 2 | 06/29/2024 20:53 PDT
COLUSA County Water And Waste Water Facility | California Department of Forestry | Tier 3, Tier 2 | 06/29/2024 21:02 PDT
COLUSA County Water And Waste Water Facility | County of Colusa | Tier 2 | 06/29/2024 21:02 PDT
Glenn County | CAO | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Glenn County | County Administrative Officer | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Glenn County | Deputy Director Oes | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Glenn County | Director Of Public Works Agency | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Glenn County | Fire Chief | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Glenn County | General | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Glenn County | Sheriff | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Glenn County Communication Facility | American Tower Corporation | Tier 2 | 06/29/2024 21:02 PDT
Glenn County Communication Facility | AT&T Services Inc | HFRA, Tier 2 | 06/29/2024 20:53 PDT
Glenn County Communication Facility | Verizon | Tier 2 | 06/29/2024 20:53 PDT
Glenn County Emergency Services Facility | County Of Glenn | Tier 2 | 06/29/2024 21:02 PDT
Glenn County Emergency Services Facility | Elk Creek Fire District | Tier 2 | 06/29/2024 20:53 PDT
GLENN County Water And Waste Water Facility | Elk Creek Community Service | Tier 2 | 06/29/2024 20:53 PDT
Glenn County Tribal | Interim Tribal Secretary | HFRA | 06/29/2024 20:58 PDT
Glenn County Tribal | Tribal Administrator | HFRA | 06/29/2024 20:58 PDT
Lake County | County Administration | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Administrator | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Battalion Chief | Tier 2 | 06/29/2024 21:06 PDT
Lake County | Board Chair | Tier 2 | 06/29/2024 21:06 PDT
Lake County | Chair of The Board | Tier 2 | 06/29/2024 21:06 PDT
Lake County | City Manager | Tier 2 | 06/29/2024 21:06 PDT
Lake County | Council Member | Tier 2 | 06/29/2024 21:06 PDT
Lake County | County Administrative Officer | Tier 2 | 06/29/2024 20:58 PDT
Lake County | County Supervisor, District 4 | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Dispatch | Tier 2 | 06/29/2024 20:58 PDT
Lake County | District 3 County Supervisor | Tier 2 | 06/29/2024 20:58 PDT
Lake County | District 5 Supervisor | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Emergency Services Manager | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Fire Chief | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Health Services Director | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Lieutenant | Tier 2 | 06/29/2024 20:58 PDT
Lake County | Mayor | Tier 2 | 06/29/2024 21:06 PDT
Lake County | Sheriff | Tier 2 | 06/29/2024 20:58 PDT
Lake County Communication Facility | AT&T Mobility LLC | Tier 2 | 07/01/2024 12:18 PDT
Lake County Communication Facility | AT&T Services Inc | Tier 2 | 06/29/2024 20:53 PDT
Lake County Communication Facility | GTE Mobile Net of California LP | Tier 3 | 07/01/2024 12:18 PDT
Lake County Communication Facility | Mediacom California LLC | Tier 2 | 07/01/2024 12:51 PDT
Napa County | County Administration | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Board Chair | Tier 2 | 06/29/2024 21:06 PDT
Napa County | County Clerk/Recorder | Tier 2 | 06/29/2024 21:06 PDT
Napa County | County Executive Officer | Tier 2 | 06/29/2024 21:06 PDT
Napa County | Deputy Chief of Operations | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Emergency Services Officer | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Fire Chief | Tier 2 | 06/29/2024 20:58 PDT
Napa County | GIS | Tier 2 | 06/29/2024 20:58 PDT
Napa County | General | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Interim County Executive Officer | Tier 2 | 06/29/2024 21:06 PDT
Napa County | MHOAC | Tier 2 | 06/29/2024 21:06 PDT
Napa County | Sheriff | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Supervisor | Tier 2 | 06/29/2024 20:58 PDT
Napa County | Under-Sheriff | Tier 2 | 06/29/2024 20:58 PDT
Napa County CCA | General | Tier 2 | 06/29/2024 20:58 PDT
Napa County Communication Facility | AT&T Mobility LLC | Tier 2 | 06/29/2024 20:53 PDT
Napa County Communication Facility | California Highway Patrol | Tier 2 | 06/29/2024 21:02 PDT
Napa County Communication Facility | T-Mobile West Corporation | Tier 3 | 07/01/2024 12:18 PDT
Shasta County | Tribal Councilmember | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | Emergency Command Center | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Fire Chief | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | General | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Interim Tribal Administrator | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Lieutenant | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | Office of Emergency Services Coordinator | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Operations Manager | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | RDMHS | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | Sergeant | Tier 3, Tier 2 | 06/29/2024 20:58 PDT
Shasta County | Sheriff-Coroner | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Staff Chief, Northern Operations | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County | Tribal Chairman | Tier 3, Tier 2 | 06/29/2024 21:06 PDT
Shasta County Anderson | Chief Plant Operator (Wastewater Treatment Plant) | Tier 2 | 06/29/2024 20:58 PDT
Shasta County Anderson | City Manager | Tier 2 | 06/29/2024 20:58 PDT
Shasta County Anderson | Deputy Public Works Director | Tier 2 | 06/29/2024 21:06 PDT
Shasta County Anderson | Fire Chief | Tier 2 | 06/29/2024 20:58 PDT
Shasta County Anderson | Public Works Superintendent | Tier 2 | 06/29/2024 20:58 PDT
Shasta County Communication Facility | AT&T Mobility C/O Engie Ins | Footnote 1 | 06/29/2024 20:53 PDT
Shasta County Communication Facility | AT&T Mobility LLC | Tier 2 | 06/29/2024 20:53 PDT
Shasta County Communication Facility | AT&T Services Inc | Tier 3, Tier 2 | 06/29/2024 20:53 PDT
Shasta County Communication Facility | Charter Communications Holding Company LLC | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | Frontier Communications | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | Frontier Communications Corporation Dip | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 06/29/2024 20:53 PDT
Shasta County Communication Facility | Happy Valley Telephone Co | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | Metro Pcs Inc | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | TDS Telecom | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Communication Facility | Verizon | Tier 2 | 06/29/2024 20:53 PDT
Shasta County Communication Facility | Verizon Wireless | Tier 2 | 06/29/2024 20:53 PDT
Shasta County Emergency Services Facility | California Department of Forestry | Tier 3, Tier 2 | 06/29/2024 20:53 PDT
Shasta County Emergency Services Facility | County Of Shasta | Tier 2 | 06/29/2024 20:53 PDT
Shasta County Government - Jail Facility | California Department of Corrections | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Other Facility | California Department of Forestry | Tier 2 | 06/29/2024 21:02 PDT
Shasta County Other Facility | Happy Valley Telephone Co | Tier 2 | 06/29/2024 21:02 PDT
SHASTA County Water And Waste Water Facility | US Bureau of Reclamation | Tier 3 | 06/29/2024 21:02 PDT
Solano County | County Administration | Tier 2 | 06/29/2024 21:06 PDT
Solano County | Board Chair | Tier 2 | 06/29/2024 21:06 PDT
Solano County | County Administrator | Tier 2 | 06/29/2024 21:06 PDT
Solano County | County Clerk | Tier 2 | 06/29/2024 21:06 PDT
Solano County | Dispatch | Tier 2 | 06/29/2024 21:06 PDT
Solano County | Emergency | Tier 2 | 06/29/2024 21:06 PDT
Solano County | Fire Chief | Tier 2 | 06/29/2024 20:58 PDT
Solano County | MHOAC - EMS Administrator | Tier 2 | 06/29/2024 20:58 PDT
Solano County | Sheriff | Tier 2 | 06/29/2024 21:06 PDT
Solano County | Supervisor | Tier 2 | 06/29/2024 20:58 PDT
Solano County CCA | General | Tier 2 | 06/29/2024 20:58 PDT
Solano County Communication Facility | American Tower Corp | Tier 2 | 06/29/2024 21:02 PDT
Solano County Communication Facility | American Tower Corporation | Tier 2 | 06/29/2024 21:02 PDT
Solano County Communication Facility | AT&T Services Inc | Tier 2 | 06/29/2024 20:53 PDT
Solano County Communication Facility | Crown Castle International | Tier 2 | 06/29/2024 21:02 PDT
Solano County Communication Facility | Verizon | Tier 2 | 06/29/2024 21:02 PDT
Sonoma County | County Administration | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | 1st District Sonoma County Supervisor | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Board Chair | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Board Vice Chair | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Community Alert & Warning Manager | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Deputy Director | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | Director | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | Division Chief | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | EMS | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | EMS Dispatch | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Fire Captain | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | MHOAC | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | Main Office | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Sheriff | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Sheriff Dispatch | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Sheriff's Liaison | Tier 3 | 07/01/2024 12:32 PDT
Sonoma County | Staff Duty Officer | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County | Supervisor | Tier 3 | 07/01/2024 12:47 PDT
Sonoma County CCA | General | Tier 3 | 07/01/2024 12:32 PDT
Tehama County | Chief Administrator | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Tehama County | Communications Supervisor | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Tehama County | County Clerk / Recorder | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Tehama County | Lieutenant And Oes Manager | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Tehama County | Oes Director | HFRA, Tier 2 | 06/29/2024 20:58 PDT
Tehama County | Sheriff | HFRA, Tier 2 | 06/29/2024 21:06 PDT
Tehama County Corning | City Clerk | Tier 2 | 06/29/2024 21:06 PDT
Tehama County Corning | City Manager | Tier 2 | 06/29/2024 21:06 PDT
Tehama County Corning | Police Chief | Tier 2 | 06/29/2024 20:58 PDT
Tehama County Red Bluff | Chief Of Police | Tier 2 | 06/29/2024 20:58 PDT
Tehama County Red Bluff | City Manager | Tier 2 | 06/29/2024 20:58 PDT
Tehama County Communication Facility | AT&T Mobility | Tier 2 | 06/29/2024 20:53 PDT
Tehama County Communication Facility | AT&T Mobility LLC | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Communication Facility | AT&T Services Inc | Tier 2 | 06/29/2024 20:53 PDT
Tehama County Communication Facility | Ducor Telephone Co | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Communication Facility | Ducor Telephone Corp | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Emergency Services Facility | California Department of Forestry | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Government - Jail Facility | California Department of Corrections | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Other Facility | Burns, Sherri | Tier 2 | 06/29/2024 20:53 PDT
Tehama County Other Facility | California Department of Forestry | Tier 2 | 06/29/2024 21:02 PDT
Tehama County Other Facility | Ducor Telephone Co | Tier 2 | 06/29/2024 21:02 PDT
Yolo County | County Administration | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | Board Chair | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | County Administrator | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | County Clerk-Recorder | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | County Oes Supervisor | Tier 2 | 06/29/2024 20:58 PDT
Yolo County | Deputy County Administrator | Tier 2 | 06/29/2024 20:58 PDT
Yolo County | Dispatch | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | Ems Administrator | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | Fire Chief | Tier 2 | 06/29/2024 20:58 PDT
Yolo County | Non-Emergency | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | Sheriff | Tier 2 | 06/29/2024 21:06 PDT
Yolo County | Supervisor | Tier 2 | 06/29/2024 21:06 PDT
Yolo County CCA | General | Tier 2 | 06/29/2024 20:58 PDT
Yolo County Communication Facility | AT&T Mobility LLC | Tier 2 | 06/29/2024 20:53 PDT
Yolo County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 06/29/2024 20:53 PDT

## Table E-1
Table E-1: Community Resource Centers Provided by PG&E
# | County | Site Name | Address | Operating Hours (PDT) |  |  |  | Total Visitors | Indoor / Outdoor | Amenities Provided
|  |  |  | Day 1 | Day 2 | Day 3 | Day 4
|  |  |  | 2024-07-02 | 2024-07-03 | 2024-07-04 | 2024-07-05
1 | Butte | Concow Elementary School | 11679 Nelson Bar Rd | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 58 | Outdoor* | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
2 | Colusa | Stonyford Community Hall | 229 Market St | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 156 | Indoor | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
3 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309 | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 37 | Outdoor* | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
4 | Lake | Twin Pine Casino and Hotel | 22223 CA- 29 | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 165 | Indoor | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
5 | Shasta | Happy Valley Community Center | 5400 Happy Valley Rd | 0800 - 2200 | 0800 – 1800** | 0800 – 2200 | 0800 - 1400 | 36 | Indoor | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
6 | Shasta | Dignity Health Mercy Oaks | 100 Mercy Oaks Dr | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 54 | Indoor | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
7 | Tehama | Rancho Tehama Association | 17605 Park Terrace Road | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 804 | Outdoor* | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
9 | Tehama | Noland Park | 19001 Bowman Rd | 0800 - 2200 | 0800 - 2200 | 0800 - 2200 | 0800 - 1400 | 67 | Outdoor* | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Cooling, Seating, and Ice.
*Cooling and ice were added as additional amenities due to extreme heat.
**The Happy Valley Community Center closed temporarily on Day two due to a wildfire evacuation.